## generator_costs
note: we assume that cogen plants have 3/4 of the capital cost and fixed cost of a pure-electric plant, (to reflect shared infrastructure for cogen), but the same variable operating costs.
all dispatch data from TEPPC_Generator_Categories
technology_id | technology | price_and_dollar_year | min_build_year | fuel | $year_of_costs | interest_between_price_year_and_cost_year | cost_for_which_year? | overnight_cost | fixed_o_m | var_o_m | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | overnight_cost_change | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | baseload | flexible_baseload | dispatchable | cogen | min_build_capacity | can_build_new | competes_for_space | ccs | storage | storage_efficiency | max_store_rate | max_spinning_reserve_fraction_of_capacity | heat_rate_penalty_spinning_reserve | minimum_loading | deep_cycling_penalty | tech_name_again | Data_Source
1 | CCGT | 2007 | 2011 | Gas | 2009 | 0.93 | 2009 | 989000 | 7170 | 2.65 | 945115.8814 | 6668.1 | 2.4645 | -0.0135 | 91289 | 6.47 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | CCGT | CEC COG Model Version 2.02-4-5-10; we picked the advanced CCGT technology (H Frame) for the new CCGT plants
103 | CCGT_Cogen | 2007 | 2011 | Gas | [6 empty] | 751905 | 5789.25 | 2.7621 | -0.0135 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CCGT_Cogen | Same as new CCGT, 75% capital cost and fixed cost
110 | CCGT_Cogen_CCS | 2007 | 2016 | Gas_CCS | [6 empty] | 1495433.5736 | 20784.0188 |  | -0.018174 | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CCGT_Cogen_CCS | Same as CCGT_CCS; 75% capital cost and fixed cost
34 | CCGT_CCS | 2007 | 2016 | Gas_CCS | 2010 | 0.9161 | 2010 | 2060000 | 30250 | 6.25 | 1993911.4315 | 27712.025 | 5.7256 | -0.018174 | 91289 | 7.525 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | CCGT_CCS | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates are the same as CCGT
20 | CCGT_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 1078000 | 8300 | 2.97 | 1002540 | 7719 | 2.7621 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | CCGT_EP | CEC COG Model Version 2.02-4-5-10; we picked the duct firing CCGT turbine for the existing CCGT technology
32 | CCGT_Cogen_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 808500 | 6225 | 2.97 | 751905 | 5789.25 | 2.7621 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CCGT_Cogen_EP | Same as existing CCGT, 75% capital cost and fixed cost
2 | Gas_Combustion_Turbine | 2007 | 2011 | Gas | 2009 | 0.93 | 2009 | 826000 | 16330 | 3.66 | 790790.7966 | 15186.9 | 3.4038 | -0.0144 | 91289 | 8.55 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Gas_Combustion_Turbine | CEC COG Model Version 2.02-4-5-10; we picked the advanced combustion turbine as the new technology
101 | Gas_Combustion_Turbine_Cogen | 2007 | 2011 | Gas | [6 empty] | 857925 | 12136.5 | 3.8688 | -0.0144 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Combustion_Turbine_Cogen | Same as gas combustion turbines, 75% capital cost and fixed cost
111 | Gas_Combustion_Turbine_Cogen_CCS | 2007 | 2016 | Gas_CCS | [6 empty] | 1379689.76 | 27173.1188 |  | -0.019385 | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Combustion_Turbine_Cogen_CCS | Same as gas combustion turbine CCS; 75% capital cost and fixed cost
35 | Gas_Combustion_Turbine_CCS | 2007 | 2016 | Gas_CCS | [6 empty] | 1839586.3466 | 36230.825 | 7.7133 | -0.019385 | 91289 | 9.9442 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Gas_Combustion_Turbine_CCS | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for CCGT; we assumed CCS combustion turbine heat rate increases by the same percentage relative to non-CCS combustion turbines as CCS to non-CCS CCGT heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates
17 | Gas_Combustion_Turbine_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 1230000 | 17400 | 4.16 | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Gas_Combustion_Turbine_EP | CEC COG Model Version 2.02-4-5-10; we picked 100 MW combustion turbine as the existing technology
29 | Gas_Combustion_Turbine_Cogen_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 922500 | 13050 | 4.16 | 857925 | 12136.5 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Combustion_Turbine_Cogen_EP | Same as existing combustion turbines, 75% capital cost and fixed cost
104 | Gas_Internal_Combustion_Engine_Cogen | 2007 | 2011 | Gas | [6 empty] | 857925 | 30000 | 3.8688 | -0.0144 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Internal_Combustion_Engine_Cogen | Same as Gas_Internal_Combustion_Engine_Cogen_EP (which already includes the 75% of capital and fixed costs)
112 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2007 | 2016 | Gas_CCS | [6 empty] | 1379689.76 | 27173.1188 |  | -0.019385 | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Internal_Combustion_Engine_Cogen_CCS | Same as Gas_Combustion_Turbine_Cogen_CCS
24 | Gas_Internal_Combustion_Engine_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 1230000 | 17400 | 4.16 | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Gas_Internal_Combustion_Engine_EP | Same as existing gas combustion turbines
40 | Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 0 | Gas | 2009 | 0.93 | 2009 | 922500 | 13050 | 4.16 | 857925 | 30000 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Internal_Combustion_Engine_Cogen_EP | Same as existing Gas Internal Combustion Engine, 75% capital cost and fixed cost
102 | Gas_Steam_Turbine_Cogen | 2007 | 2011 | Gas | [6 empty] | 326250 | 20797.5 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Steam_Turbine_Cogen | Same as existing gas steam turbines, 75% capital cost and fixed cost
113 | Gas_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Gas_CCS | [6 empty] | 1112846.6625 | 36580.4438 |  |  | 91289 |  | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Steam_Turbine_Cogen_CCS | Capital and fixed cost equal to 75% of Gas_Steam_Turbine_EP + difference between CCGT_CCS and CCGT, other flags like Gas_Steam_Turbine_Cogen (except ccs)
19 | Gas_Steam_Turbine_EP | 2007 | 0 | Gas | 2007 | 1 | 2000 | 435000 | 27730 | 3.47 | 435000 | 27730 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.03 | 0 | 0 | Gas_Steam_Turbine_EP | ReEDs Sheet, took OGS (Oil Gas Steam)
31 | Gas_Steam_Turbine_Cogen_EP | 2007 | 0 | Gas | 2007 | 1 | 2000 | 326250 | 20797.5 | 3.47 | 326250 | 20797.5 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Gas_Steam_Turbine_Cogen_EP | Same as existing gas steam turbines, 75% capital cost and fixed cost
60 | DistillateFuelOil_Combustion_Turbine_EP | 2007 | 0 | DistillateFuelOil | 2009 | 0.93 | 2009 | 1230000 | 17400 | 4.16 | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | DistillateFuelOil_Combustion_Turbine_EP | Same as existing Gas Combustion Turbine
61 | DistillateFuelOil_Internal_Combustion_Engine_EP | 2007 | 0 | DistillateFuelOil | 2009 | 0.93 | 2009 | 1230000 | 17400 | 4.16 | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | DistillateFuelOil_Internal_Combustion_Engine_EP | Same as existing Gas Combustion Turbine
8 | Bio_Gas | 2007 | 2011 | Bio_Gas | 2007 | 1 | 2008 | 2377000 | 114250 | 0.01 | 2411728.8961 | 114250 | 0.01 | -0.0144 | 91289 | 13.648 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to gas combustion turbine
36 | Bio_Gas_CCS | 2007 | 2016 | Bio_Gas_CCS | [6 empty] | 4509319.9962 | 156337.85 | 13.7682 | -0.019385 | 91289 | 18.0989 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_CCS | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for gas combustion turbine; as biogas contains 50% pre-combustion CO2, we assumed that the biogas-CCS heat rate was the biogas non-CCS heat rate plus double the difference between CCS to non-CCS combustion turbine heat rates; we also assume a similar multiplier to variable costs
105 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2007 | 2011 | Bio_Gas | [6 empty] | 1782750 | 114250 | 0.01 | -0.0144 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_Internal_Combustion_Engine_Cogen | Same as new Biogas, 75% capital cost and fixed cost
114 | Bio_Gas_Internal_Combustion_Engine_Cogen_CCS | 2007 | 2016 | Bio_Gas_CCS | [6 empty] | 3381989.9971 | 117253.3875 |  | -0.019385 | 91289 |  | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_Internal_Combustion_Engine_Cogen_CCS | Same as new Biogas_CCS, 75% capital cost and fixed cost
80 | Bio_Gas_Internal_Combustion_Engine_EP | 2007 | 2011 | Bio_Gas | 2007 | 1 | 2008 | 2377000 | 114250 | 0.01 | 2377000 | 114250 | 0.01 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_Internal_Combustion_Engine_EP | Same as new Biogas
81 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 2011 | Bio_Gas | 2007 | 1 | 2008 | 1782750 | 85687.5 | 0.01 | 1782750 | 114250 | 0.01 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | Same as new Biogas, 75% capital cost and fixed cost
82 | Bio_Gas_Steam_Turbine_EP | 2007 | 0 | Bio_Gas | [6 empty] | 2055938.0995 | 126793.1 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Gas_Steam_Turbine_EP | Everything but costs same as gas steam turbine; captial and fixed costs are assumed to be the gas steam turbine cost plus the difference between biogas and gas combustion turbine
106 | Bio_Liquid_Steam_Turbine_Cogen | 2007 | 2011 | Bio_Liquid | [6 empty] | 2292723.0992 | 69401.25 | 4.1292 | -0.0055 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Liquid_Steam_Turbine_Cogen | Same as new biomass steam turbine, 75% capital cost and fixed cost
115 | Bio_Liquid_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Bio_Liquid_CCS | [6 empty] | 2966454.2026 | 92445.7455 |  | -0.013707 | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Liquid_Steam_Turbine_Cogen_CCS | Costs are same as Bio_Solid_Steam_Turbine_Cogen_CCS; flags same as Bio_Liquid_Steam_Turbine_Cogen
85 | Bio_Liquid_Steam_Turbine_Cogen_EP | 2007 | 0 | Bio_Liquid | [6 empty] | 2292723.0992 | 69401.25 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Liquid_Steam_Turbine_Cogen_EP | Same as new biomass steam turbine, 75% capital cost and fixed cost
10 | Biomass_IGCC | 2007 | 2011 | Bio_Solid | 2009 | 0.93 | 2009 | 2995000 | 150000 | 3.99 | 2869663.4676 | 139500 | 3.7107 | -0.0148 | 91289 | 10.5 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Biomass_IGCC | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to coal IGCC
37 | Biomass_IGCC_CCS | 2007 | 2016 | Bio_Solid_CCS | [6 empty] | 4942575.6502 | 158188.44 | 5.0043 | -0.017048 | 91289 | 12.9138 | 2 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Biomass_IGCC_CCS | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for Coal IGCC; we assumed CCS biomass IGCC heat rate increases by the same percentage relative to non-CCS biomass IGCC as CCS to non-CCS coal IGCC heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates
9 | Biomass_Steam_Turbine | 2007 | 2011 | Bio_Solid | 2009 | 0.93 | 2009 | 3251000 | 99500 | 4.44 | 3056964.1323 | 92535 | 4.1292 | -0.0055 | 91289 | 10.5 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Biomass_Steam_Turbine | CEC COG Model Version 2.02-4-5-10; we chose the fluidized bed biomass technology because it's more advanced
107 | Bio_Solid_Steam_Turbine_Cogen | 2007 | 2011 | Bio_Solid | [6 empty] | 2292723.0992 | 69401.25 | 4.1292 | -0.0055 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Solid_Steam_Turbine_Cogen | Same as new biomass steam turbine, 75% capital cost and fixed cost
116 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Bio_Solid_CCS | [6 empty] | 2966454.2026 | 92445.7455 |  | -0.013707 | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Solid_Steam_Turbine_Cogen_CCS | Capital and fixed cost equal to cost for Bio_Solid_Steam_Turbine_Cogen plus the difference between Coal_Steam_Turbine_Cogen_CCS and Coal_Steam_Turbine_Cogen; overnight cost change like Coal_Steam_Turbine_Cogen_CCS; other params like Bio_Solid_Steam_Turbine_Cogen
90 | Bio_Solid_Steam_Turbine_EP | 2007 | 0 | Bio_Solid | [6 empty] | 3056964.1323 | 92535 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Solid_Steam_Turbine_EP | Same as new biomass steam turbine
91 | Bio_Solid_Steam_Turbine_Cogen_EP | 2007 | 0 | Bio_Solid | [6 empty] | 2292723.0992 | 69401.25 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Bio_Solid_Steam_Turbine_Cogen_EP | Same as new biomass steam turbine, 75% capital cost and fixed cost
12 | Coal_Steam_Turbine | 2007 | 2011 | Coal | 2010 | 0.9161 | 2010 | 2844000 | 29670 | 4.25 | 2700659.1621 | 27180.687 | 3.8934 | -0.0119 | 91289 | 8.8 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | Coal_Steam_Turbine | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; we assume the same lifetime, construction time, construction cost breakdown, and outage rates as for Coal IGCC
39 | Coal_Steam_Turbine_CCS | 2007 | 2016 | Coal_CCS | 2010 | 0.9161 | 2010 | 4579000 | 63210 | 9.05 | 4372159.3379 | 57906.681 | 8.2907 | -0.013707 | 91289 | 12 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | Coal_Steam_Turbine_CCS | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; chose the dual unit rather than the single unit costs because if we're installing CCS, we're likley installing a lot; the lifetime, construction time, construction cost breakdown, and outage rates are the same as Coal Steam Turbine
100 | Coal_Steam_Turbine_Cogen | 2007 | 2011 | Coal | [6 empty] | 2605388.4 | 20385.5153 | 3.8934 | -0.0119 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Coal_Steam_Turbine_Cogen | Same as new coal steam turbines, 75% capital cost and fixed cost
117 | Coal_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Coal_CCS | [6 empty] | 3279119.5034 | 43430.0108 |  | -0.013707 | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Coal_Steam_Turbine_Cogen_CCS | Capital and fixed cost equal to 75% of Coal_Steam_Turbine_CCS
18 | Coal_Steam_Turbine_EP | 2007 | 0 | Coal | 2010 | 0.9161 | 2010 | 2844000 | 29670 | 4.25 | 2605388.4 | 27180.687 | 3.8934 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.05 | Coal_Steam_Turbine_EP | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; we assume the same lifetime, construction time, construction cost breakdown, and outage rates as for Coal IGCC
30 | Coal_Steam_Turbine_Cogen_EP | 2007 | 0 | Coal | 2010 | 0.9161 | 2010 | 2844000 | 22252.5 | 4.25 | 2605388.4 | 20385.5153 | 3.8934 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Coal_Steam_Turbine_Cogen_EP | Same as existing coal steam turbines, 75% capital cost and fixed cost
11 | Coal_IGCC | 2007 | 2011 | Coal | 2010 | 0.9161 | 2010 | 3221000 | 48900 | 6.87 | 3085747.5899 | 44797.29 | 6.2936 | -0.0148 | 91289 | 8.7 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | Coal_IGCC | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates come from the CEC COG Model Version 2.02-4-5-10
38 | Coal_IGCC_CCS | 2007 | 2016 | Coal_CCS | 2010 | 0.9161 | 2010 | 5348000 | 69300 | 8.04 | 5158659.7725 | 63485.73 | 7.3654 | -0.017048 | 91289 | 10.7 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | Coal_IGCC_CCS | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates are the same as Coal IGCC
13 | Nuclear | 2007 | 2011 | Uranium | 2009 | 0.93 | 2009 | 3950000 | 147700 | 5.18 | 3673500 | 137361 | 4.8174 | 0 | 91289 | 10.4 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.0272 | 0.1112 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Nuclear | CEC COG Model Version 2.02-4-5-10
22 | Nuclear_EP | 2007 | 0 | Uranium | 2009 | 0.93 | 2009 | 3950000 | 147700 | 5.18 | 3673500 | 137361 | 4.8174 | 0 | 91289 | 0 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.0272 | 0.1112 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Nuclear_EP | Same as new nuclear
14 | Geothermal | 2007 | 2011 | Geothermal | 2009 | 0.93 | 2009 | 4046000 | 47440 | 3.41 | 3839179.6755 | 44119.2 | 3.1713 | -0.01 | 65639 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.025 | 0.04 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Geothermal | CEC COG Model Version 2.02-4-5-10; we chose the binary geothermal plants because they are more advanced
21 | Geothermal_EP | 2007 | 0 | Geothermal | 2009 | 0.93 | 2009 | 3706000 | 58380 | 3.8 | 3446580 | 54293.4 | 3.534 | 0 | 91289 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.025 | 0.04 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Geothermal_EP | CEC COG Model Version 2.02-4-5-10; we picked dual flash as the existing geothermal technology
6 | Residential_PV | 2007 | 2011 | Solar | 2009 | 0.93 | 2010 | 5950000 | 10526 | 0 | 6423526.7409 | 9789.18 | 0 | -0.0485 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Residential_PV | DOE Solar Program Costs, took 2020 value for fixed O+M, 10% added to capital costs to go from utility to distributed, but also assumed a 5% declination rate; forced outage rate is from the CEC COG Model
25 | Commercial_PV | 2007 | 2011 | Solar | 2009 | 0.93 | 2010 | 5100000 | 10526 | 0 | 5457557.916 | 9789.18 | 0 | -0.0457 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Commercial_PV | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, CEC COG Model for construction time and cost fractions, as well as for forced outage rate
26 | Central_PV | 2007 | 2011 | Solar | 2009 | 0.93 | 2010 | 4060000 | 10526 | 0 | 4231906.5281 | 9789.18 | 0 | -0.0373 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Central_PV | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, CEC COG Model for construction time and cost fractions, as well as for forced outage rate
3 | Concentrating_PV | 2007 | 2011 | Solar | 2010 | 0.9161 | 2010 | 4700000 | 17000 | 0 | 5231490.028 | 15573.7 | 0 | -0.062859 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 25 | 0.0027 | 0.0054 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Concentrating_PV | CPV Consortium numbers (It's more or less SolFocus)
27 | CSP_Trough_No_Storage | 2007 | 2011 | Solar | 2009 | 0.93 | 2009 | 3687000 | 68000 | 0 | 3490417.0028 | 63240 | 0 | -0.00885 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.016 | 0.022 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CSP_Trough_No_Storage | CEC COG Model Version 2.02-4-5-10
7 | CSP_Trough_6h_Storage | 2007 | 2012 | Solar | 2009 | 0.93 | 2009 | 6278000 | 68000 | 0 | 5943270.3942 | 63240 | 0 | -0.00885 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.016 | 0.022 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CSP_Trough_6h_Storage | CEC COG Model Version 2.02-4-5-10; the overnight cost is adjusted from the non-storage CSP overnight-cost based on the difference in the storage and non-storage CSP from the Solar Advisor Model; the construction time of 1 year is probably too low
5 | Offshore_Wind | 2007 | 2011 | Wind | 2009 | 0.93 | 2009 | 5588000 | 27400 | 10.18 | 5334639.0616 | 25482 | 9.4674 | -0.013 | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0262 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Offshore_Wind | CEC COG Model Version 2.02-4-5-10
4 | Wind | 2007 | 2011 | Wind | 2009 | 0.93 | 2009 | 1990000 | 13700 | 5.09 | 1869346.7337 | 12741 | 4.7337 | -0.005 | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0139 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wind | CEC COG Model Version 2.02-4-5-10
23 | Wind_EP | 2007 | 0 | Wind | 2009 | 0.93 | 2009 | 1990000 | 13700 | 5.09 | 1850700 | 12741 | 4.7337 | 0 | 91289 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0139 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wind_EP | Same as new wind except for a generic connect cost
15 | Hydro_NonPumped | 2007 | 0 | Water | 2010 | 0.9161 | 2010 | 3076000 | 13440 | 0 | 2817923.6 | 12312.384 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.051 | 0.094 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hydro_NonPumped | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; construction cost breakdown comes from the ReEDs Sheet; outage rates are from the CEC COG Model
16 | Hydro_Pumped | 2007 | 0 | Water | 2010 | 0.9161 | 2010 | 5595000 | 13030 | 0 | 5125579.5 | 11936.783 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.051 | 0.094 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1 | 0 | 0 | 0 | 0 | Hydro_Pumped | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; construction cost breakdown comes from the ReEDs Sheet; outage rates are the same as hydro
28 | Compressed_Air_Energy_Storage | 2007 | 2011 | Gas | 2010 | 0.9161 | 2010 | 1200000 | 10310 | 3.1 | 1103287.0692 | 9444.991 | 2.8399 | -0.0012 | 91289 | 4.4 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0.817 | 1.2 | 0.3 | 0.087 | 0 | 0 | Compressed_Air_Energy_Storage | ReEDs Sheet; also Sullivan et al (2008), NREL/CP-670-43510 Conference Paper for o&m costs, declanation rate, etc; $1,200,000 taken as capital cost in 2010 rather than 2004 based on conversation with Hernandez, also The storage efficiency of the the storage phase of compressed air energy storage from Samir Succar and Robert H. Williams: Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power, p. 39
33 | Battery_Storage | 2007 | 2011 | Storage | 2004 | 1.1679 | 2010 | 3539000 | 22100 | 0.445 | 4202867.8683 | 25810.59 | 0.51972 | -0.0055564 | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 15 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.767 | 1 | 0 | 0 | 0 | 0 | Battery_Storage | ReEDs Sheet

## Cost CSV For Export
technology_id | technology | price_and_dollar_year | min_build_year | fuel | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | overnight_cost_change | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | baseload | flexible_baseload | dispatchable | cogen | min_build_capacity | can_build_new | competes_for_space | ccs | storage | storage_efficiency | max_store_rate | max_spinning_reserve_fraction_of_capacity | heat_rate_penalty_spinning_reserve | minimum_loading | deep_cycling_penalty | Data_Source
1 | CCGT | 2007 | 2011 | Gas | 945115.8814 | 6668.1 | 2.4645 | -0.0135 | 91289 | 6.47 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | CEC COG Model Version 2.02-4-5-10; we picked the advanced CCGT technology (H Frame) for the new CCGT plants
103 | CCGT_Cogen | 2007 | 2011 | Gas | 751905 | 5789.25 | 2.7621 | -0.0135 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new CCGT, 75% capital cost and fixed cost
110 | CCGT_Cogen_CCS | 2007 | 2016 | Gas_CCS | 1495433.5736 | 20784.0188 | 0 | -0.018174 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as CCGT_CCS; 75% capital cost and fixed cost
34 | CCGT_CCS | 2007 | 2016 | Gas_CCS | 1993911.4315 | 27712.025 | 5.7256 | -0.018174 | 91289 | 7.525 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates are the same as CCGT
20 | CCGT_EP | 2007 | 0 | Gas | 1002540 | 7719 | 2.7621 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.306 | 0 | 0 | CEC COG Model Version 2.02-4-5-10; we picked the duct firing CCGT turbine for the existing CCGT technology
32 | CCGT_Cogen_EP | 2007 | 0 | Gas | 751905 | 5789.25 | 2.7621 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0224 | 0.0602 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing CCGT, 75% capital cost and fixed cost
2 | Gas_Combustion_Turbine | 2007 | 2011 | Gas | 790790.7966 | 15186.9 | 3.4038 | -0.0144 | 91289 | 8.55 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | CEC COG Model Version 2.02-4-5-10; we picked the advanced combustion turbine as the new technology
101 | Gas_Combustion_Turbine_Cogen | 2007 | 2011 | Gas | 857925 | 12136.5 | 3.8688 | -0.0144 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as gas combustion turbines, 75% capital cost and fixed cost
111 | Gas_Combustion_Turbine_Cogen_CCS | 2007 | 2016 | Gas_CCS | 1379689.76 | 27173.1188 | 0 | -0.019385 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as gas combustion turbine CCS; 75% capital cost and fixed cost
35 | Gas_Combustion_Turbine_CCS | 2007 | 2016 | Gas_CCS | 1839586.3466 | 36230.825 | 7.7133 | -0.019385 | 91289 | 9.9442 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for CCGT; we assumed CCS combustion turbine heat rate increases by the same percentage relative to non-CCS combustion turbines as CCS to non-CCS CCGT heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates
17 | Gas_Combustion_Turbine_EP | 2007 | 0 | Gas | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | CEC COG Model Version 2.02-4-5-10; we picked 100 MW combustion turbine as the existing technology
29 | Gas_Combustion_Turbine_Cogen_EP | 2007 | 0 | Gas | 857925 | 12136.5 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing combustion turbines, 75% capital cost and fixed cost
104 | Gas_Internal_Combustion_Engine_Cogen | 2007 | 2011 | Gas | 857925 | 30000 | 3.8688 | -0.0144 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as Gas_Internal_Combustion_Engine_Cogen_EP (which already includes the 75% of capital and fixed costs)
112 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2007 | 2016 | Gas_CCS | 1379689.76 | 27173.1188 | 0 | -0.019385 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as Gas_Combustion_Turbine_Cogen_CCS
24 | Gas_Internal_Combustion_Engine_EP | 2007 | 0 | Gas | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Same as existing gas combustion turbines
40 | Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 0 | Gas | 857925 | 30000 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing Gas Internal Combustion Engine, 75% capital cost and fixed cost
102 | Gas_Steam_Turbine_Cogen | 2007 | 2011 | Gas | 326250 | 20797.5 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing gas steam turbines, 75% capital cost and fixed cost
113 | Gas_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Gas_CCS | 1112846.6625 | 36580.4438 | 0 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Capital and fixed cost equal to 75% of Gas_Steam_Turbine_EP + difference between CCGT_CCS and CCGT, other flags like Gas_Steam_Turbine_Cogen (except ccs)
19 | Gas_Steam_Turbine_EP | 2007 | 0 | Gas | 435000 | 27730 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.03 | 0 | 0 | ReEDs Sheet, took OGS (Oil Gas Steam)
31 | Gas_Steam_Turbine_Cogen_EP | 2007 | 0 | Gas | 326250 | 20797.5 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing gas steam turbines, 75% capital cost and fixed cost
60 | DistillateFuelOil_Combustion_Turbine_EP | 2007 | 0 | DistillateFuelOil | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Same as existing Gas Combustion Turbine
61 | DistillateFuelOil_Internal_Combustion_Engine_EP | 2007 | 0 | DistillateFuelOil | 1143900 | 16182 | 3.8688 | 0 | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.0413 | 0.0318 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.087 | 0 | 0 | Same as existing Gas Combustion Turbine
8 | Bio_Gas | 2007 | 2011 | Bio_Gas | 2411728.8961 | 114250 | 0.01 | -0.0144 | 91289 | 13.648 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to gas combustion turbine
36 | Bio_Gas_CCS | 2007 | 2016 | Bio_Gas_CCS | 4509319.9962 | 156337.85 | 13.7682 | -0.019385 | 91289 | 18.0989 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for gas combustion turbine; as biogas contains 50% pre-combustion CO2, we assumed that the biogas-CCS heat rate was the biogas non-CCS heat rate plus double the difference between CCS to non-CCS combustion turbine heat rates; we also assume a similar multiplier to variable costs
105 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2007 | 2011 | Bio_Gas | 1782750 | 114250 | 0.01 | -0.0144 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new Biogas, 75% capital cost and fixed cost
114 | Bio_Gas_Internal_Combustion_Engine_Cogen_CCS | 2007 | 2016 | Bio_Gas_CCS | 3381989.9971 | 117253.3875 | 0 | -0.019385 | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new Biogas_CCS, 75% capital cost and fixed cost
80 | Bio_Gas_Internal_Combustion_Engine_EP | 2007 | 2011 | Bio_Gas | 2377000 | 114250 | 0.01 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new Biogas
81 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 2011 | Bio_Gas | 1782750 | 114250 | 0.01 | 0 | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 30 | 0.0413 | 0.0318 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new Biogas, 75% capital cost and fixed cost
82 | Bio_Gas_Steam_Turbine_EP | 2007 | 0 | Bio_Gas | 2055938.0995 | 126793.1 | 3.47 | 0 | 91289 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Everything but costs same as gas steam turbine; captial and fixed costs are assumed to be the gas steam turbine cost plus the difference between biogas and gas combustion turbine
106 | Bio_Liquid_Steam_Turbine_Cogen | 2007 | 2011 | Bio_Liquid | 2292723.0992 | 69401.25 | 4.1292 | -0.0055 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new biomass steam turbine, 75% capital cost and fixed cost
115 | Bio_Liquid_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Bio_Liquid_CCS | 2966454.2026 | 92445.7455 | 0 | -0.013707 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Costs are same as Bio_Solid_Steam_Turbine_Cogen_CCS; flags same as Bio_Liquid_Steam_Turbine_Cogen
85 | Bio_Liquid_Steam_Turbine_Cogen_EP | 2007 | 0 | Bio_Liquid | 2292723.0992 | 69401.25 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new biomass steam turbine, 75% capital cost and fixed cost
10 | Biomass_IGCC | 2007 | 2011 | Bio_Solid | 2869663.4676 | 139500 | 3.7107 | -0.0148 | 91289 | 10.5 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to coal IGCC
37 | Biomass_IGCC_CCS | 2007 | 2016 | Bio_Solid_CCS | 4942575.6502 | 158188.44 | 5.0043 | -0.017048 | 91289 | 12.9138 | 2 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for Coal IGCC; we assumed CCS biomass IGCC heat rate increases by the same percentage relative to non-CCS biomass IGCC as CCS to non-CCS coal IGCC heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates
9 | Biomass_Steam_Turbine | 2007 | 2011 | Bio_Solid | 3056964.1323 | 92535 | 4.1292 | -0.0055 | 91289 | 10.5 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CEC COG Model Version 2.02-4-5-10; we chose the fluidized bed biomass technology because it's more advanced
107 | Bio_Solid_Steam_Turbine_Cogen | 2007 | 2011 | Bio_Solid | 2292723.0992 | 69401.25 | 4.1292 | -0.0055 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new biomass steam turbine, 75% capital cost and fixed cost
116 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Bio_Solid_CCS | 2966454.2026 | 92445.7455 | 0 | -0.013707 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Capital and fixed cost equal to cost for Bio_Solid_Steam_Turbine_Cogen plus the difference between Coal_Steam_Turbine_Cogen_CCS and Coal_Steam_Turbine_Cogen; overnight cost change like Coal_Steam_Turbine_Cogen_CCS; other params like Bio_Solid_Steam_Turbine_Cogen
90 | Bio_Solid_Steam_Turbine_EP | 2007 | 0 | Bio_Solid | 3056964.1323 | 92535 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new biomass steam turbine
91 | Bio_Solid_Steam_Turbine_Cogen_EP | 2007 | 0 | Bio_Solid | 2292723.0992 | 69401.25 | 4.1292 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 20 | 0.08 | 0.03 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new biomass steam turbine, 75% capital cost and fixed cost
12 | Coal_Steam_Turbine | 2007 | 2011 | Coal | 2700659.1621 | 27180.687 | 3.8934 | -0.0119 | 91289 | 8.8 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; we assume the same lifetime, construction time, construction cost breakdown, and outage rates as for Coal IGCC
39 | Coal_Steam_Turbine_CCS | 2007 | 2016 | Coal_CCS | 4372159.3379 | 57906.681 | 8.2907 | -0.013707 | 91289 | 12 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; chose the dual unit rather than the single unit costs because if we're installing CCS, we're likley installing a lot; the lifetime, construction time, construction cost breakdown, and outage rates are the same as Coal Steam Turbine
100 | Coal_Steam_Turbine_Cogen | 2007 | 2011 | Coal | 2605388.4 | 20385.5153 | 3.8934 | -0.0119 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new coal steam turbines, 75% capital cost and fixed cost
117 | Coal_Steam_Turbine_Cogen_CCS | 2007 | 2016 | Coal_CCS | 3279119.5034 | 43430.0108 | 0 | -0.013707 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Capital and fixed cost equal to 75% of Coal_Steam_Turbine_CCS
18 | Coal_Steam_Turbine_EP | 2007 | 0 | Coal | 2605388.4 | 27180.687 | 3.8934 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.05 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; we assume the same lifetime, construction time, construction cost breakdown, and outage rates as for Coal IGCC
30 | Coal_Steam_Turbine_Cogen_EP | 2007 | 0 | Coal | 2605388.4 | 20385.5153 | 3.8934 | 0 | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as existing coal steam turbines, 75% capital cost and fixed cost
11 | Coal_IGCC | 2007 | 2011 | Coal | 3085747.5899 | 44797.29 | 6.2936 | -0.0148 | 91289 | 8.7 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates come from the CEC COG Model Version 2.02-4-5-10
38 | Coal_IGCC_CCS | 2007 | 2016 | Coal_CCS | 5158659.7725 | 63485.73 | 7.3654 | -0.017048 | 91289 | 10.7 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.05 | 0.15 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; the lifetime, construction time, construction cost breakdown, and outage rates are the same as Coal IGCC
13 | Nuclear | 2007 | 2011 | Uranium | 3673500 | 137361 | 4.8174 | 0 | 91289 | 10.4 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.0272 | 0.1112 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CEC COG Model Version 2.02-4-5-10
22 | Nuclear_EP | 2007 | 0 | Uranium | 3673500 | 137361 | 4.8174 | 0 | 91289 | 0 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.0272 | 0.1112 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Same as new nuclear
14 | Geothermal | 2007 | 2011 | Geothermal | 3839179.6755 | 44119.2 | 3.1713 | -0.01 | 65639 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.025 | 0.04 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CEC COG Model Version 2.02-4-5-10; we chose the binary geothermal plants because they are more advanced
21 | Geothermal_EP | 2007 | 0 | Geothermal | 3446580 | 54293.4 | 3.534 | 0 | 91289 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.025 | 0.04 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | CEC COG Model Version 2.02-4-5-10; we picked dual flash as the existing geothermal technology
6 | Residential_PV | 2007 | 2011 | Solar | 6423526.7409 | 9789.18 | 0 | -0.0485 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DOE Solar Program Costs, took 2020 value for fixed O+M, 10% added to capital costs to go from utility to distributed, but also assumed a 5% declination rate; forced outage rate is from the CEC COG Model
25 | Commercial_PV | 2007 | 2011 | Solar | 5457557.916 | 9789.18 | 0 | -0.0457 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, CEC COG Model for construction time and cost fractions, as well as for forced outage rate
26 | Central_PV | 2007 | 2011 | Solar | 4231906.5281 | 9789.18 | 0 | -0.0373 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.02 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, CEC COG Model for construction time and cost fractions, as well as for forced outage rate
3 | Concentrating_PV | 2007 | 2011 | Solar | 5231490.028 | 15573.7 | 0 | -0.062859 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 25 | 0.0027 | 0.0054 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CPV Consortium numbers (It's more or less SolFocus)
27 | CSP_Trough_No_Storage | 2007 | 2011 | Solar | 3490417.0028 | 63240 | 0 | -0.00885 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.016 | 0.022 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CEC COG Model Version 2.02-4-5-10
7 | CSP_Trough_6h_Storage | 2007 | 2012 | Solar | 5943270.3942 | 63240 | 0 | -0.00885 | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.016 | 0.022 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CEC COG Model Version 2.02-4-5-10; the overnight cost is adjusted from the non-storage CSP overnight-cost based on the difference in the storage and non-storage CSP from the Solar Advisor Model; the construction time of 1 year is probably too low
5 | Offshore_Wind | 2007 | 2011 | Wind | 5334639.0616 | 25482 | 9.4674 | -0.013 | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0262 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CEC COG Model Version 2.02-4-5-10
4 | Wind | 2007 | 2011 | Wind | 1869346.7337 | 12741 | 4.7337 | -0.005 | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0139 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CEC COG Model Version 2.02-4-5-10
23 | Wind_EP | 2007 | 0 | Wind | 1850700 | 12741 | 4.7337 | 0 | 91289 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.02 | 0.0139 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Same as new wind except for a generic connect cost
15 | Hydro_NonPumped | 2007 | 0 | Water | 2817923.6 | 12312.384 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.051 | 0.094 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; construction cost breakdown comes from the ReEDs Sheet; outage rates are from the CEC COG Model
16 | Hydro_Pumped | 2007 | 0 | Water | 5125579.5 | 11936.783 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.051 | 0.094 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1 | 0 | 0 | 0 | 0 | "Updated Capital Cost Estimates for Electricity Generation Plants," US EIA, November 2010; construction cost breakdown comes from the ReEDs Sheet; outage rates are the same as hydro
28 | Compressed_Air_Energy_Storage | 2007 | 2011 | Gas | 1103287.0692 | 9444.991 | 2.8399 | -0.0012 | 91289 | 4.4 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0.817 | 1.2 | 0.3 | 0.087 | 0 | 0 | ReEDs Sheet; also Sullivan et al (2008), NREL/CP-670-43510 Conference Paper for o&m costs, declanation rate, etc; $1,200,000 taken as capital cost in 2010 rather than 2004 based on conversation with Hernandez, also The storage efficiency of the the storage phase of compressed air energy storage from Samir Succar and Robert H. Williams: Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power, p. 39
33 | Battery_Storage | 2007 | 2011 | Storage | 4202867.8683 | 25810.59 | 0.51972 | -0.0055564 | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 15 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.767 | 1 | 0 | 0 | 0 | 0 | ReEDs Sheet

## costs_by_investment_period
Resultant Capital Costs ($2007/MW) in Investment Period Years
technology | 2010 | 2014 | 2018 | 2022 | 2026 | Cost Declination Rate (%/yr)
CCGT | 0.90735 | 0.85934 | 0.81387 | 0.7708 | 0.73001 | 1.35
Gas_Combustion_Turbine | 0.75712 | 0.71444 | 0.67417 | 0.63617 | 0.60031 | 1.44
Concentrating_PV | 4.3057 | 3.3209 | 2.5614 | 1.9756 | 1.5238 | 6.2859
Wind | 1.8414 | 1.8049 | 1.7691 | 1.7339 | 1.6995 | 0.5
Offshore_Wind | 5.1293 | 4.8677 | 4.6195 | 4.3839 | 4.1604 | 1.3
Residential_PV | 5.5335 | 4.5356 | 3.7177 | 3.0472 | 2.4977 | 4.85
CSP_Trough_6h_Storage | 5.7869 | 5.5847 | 5.3896 | 5.2014 | 5.0197 | 0.885
Bio_Gas | 2.309 | 2.1789 | 2.0561 | 1.9402 | 1.8308 | 1.44
Biomass_Steam_Turbine | 3.0068 | 2.9412 | 2.877 | 2.8142 | 2.7528 | 0.55
Biomass_IGCC | 2.7441 | 2.5852 | 2.4356 | 2.2945 | 2.1617 | 1.48
Coal_IGCC | 2.9508 | 2.7799 | 2.619 | 2.4673 | 2.3245 | 1.48
Coal_Steam_Turbine | 2.6054 | 2.4836 | 2.3674 | 2.2567 | 2.1512 | 1.19
Nuclear | 3.6735 | 3.6735 | 3.6735 | 3.6735 | 3.6735 | 0
Geothermal | 3.7252 | 3.5784 | 3.4374 | 3.3019 | 3.1718 | 1
Hydro_NonPumped | 2.8179 | 2.8179 | 2.8179 | 2.8179 | 2.8179 | 0
Hydro_Pumped | 5.1256 | 5.1256 | 5.1256 | 5.1256 | 5.1256 | 0
Gas_Combustion_Turbine_EP | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 0
Coal_Steam_Turbine_EP | 2.6054 | 2.6054 | 2.6054 | 2.6054 | 2.6054 | 0
Gas_Steam_Turbine_EP | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0
CCGT_EP | 1.0025 | 1.0025 | 1.0025 | 1.0025 | 1.0025 | 0
Geothermal_EP | 3.4466 | 3.4466 | 3.4466 | 3.4466 | 3.4466 | 0
Nuclear_EP | 3.6735 | 3.6735 | 3.6735 | 3.6735 | 3.6735 | 0
Wind_EP | 1.8507 | 1.8507 | 1.8507 | 1.8507 | 1.8507 | 0
Gas_Internal_Combustion_Engine_EP | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 0
Commercial_PV | 4.743 | 3.9336 | 3.2624 | 2.7057 | 2.2439 | 4.57
Central_PV | 3.7758 | 3.2432 | 2.7857 | 2.3928 | 2.0552 | 3.73
CSP_Trough_No_Storage | 3.3986 | 3.2798 | 3.1653 | 3.0547 | 2.948 | 0.885
Compressed_Air_Energy_Storage | 1.0993 | 1.0941 | 1.0888 | 1.0836 | 1.0784 | 0.12
Gas_Combustion_Turbine_Cogen_EP | 0.85793 | 0.85793 | 0.85793 | 0.85793 | 0.85793 | 0
Coal_Steam_Turbine_Cogen_EP | 2.6054 | 2.6054 | 2.6054 | 2.6054 | 2.6054 | 0
Gas_Steam_Turbine_Cogen_EP | 0.32625 | 0.32625 | 0.32625 | 0.32625 | 0.32625 | 0
CCGT_Cogen_EP | 0.75191 | 0.75191 | 0.75191 | 0.75191 | 0.75191 | 0
Battery_Storage | 4.1332 | 4.0421 | 3.953 | 3.8659 | 3.7807 | 0.55564
CCGT_CCS | 1.8872 | 1.7537 | 1.6296 | 1.5144 | 1.4072 | 1.8174
Gas_Combustion_Turbine_CCS | 1.7347 | 1.604 | 1.4832 | 1.3715 | 1.2682 | 1.9385
Bio_Gas_CCS | 4.2521 | 3.9319 | 3.6358 | 3.3619 | 3.1087 | 1.9385
Biomass_IGCC_CCS | 4.6941 | 4.3821 | 4.0908 | 3.8189 | 3.5651 | 1.7048
Coal_IGCC_CCS | 4.8993 | 4.5737 | 4.2697 | 3.9859 | 3.7209 | 1.7048
Coal_Steam_Turbine_CCS | 4.1948 | 3.9695 | 3.7563 | 3.5545 | 3.3636 | 1.3707
Gas_Internal_Combustion_Engine_Cogen_EP | 0.85793 | 0.85793 | 0.85793 | 0.85793 | 0.85793 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
DistillateFuelOil_Combustion_Turbine_EP | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 0
DistillateFuelOil_Internal_Combustion_Engine_EP | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 1.1439 | 0
Bio_Gas_Internal_Combustion_Engine_EP | 2.377 | 2.377 | 2.377 | 2.377 | 2.377 | 0
Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 1.7828 | 1.7828 | 1.7828 | 1.7828 | 1.7828 | 0
Bio_Gas_Steam_Turbine_EP | 2.0559 | 2.0559 | 2.0559 | 2.0559 | 2.0559 | 0
Bio_Liquid_Steam_Turbine_Cogen_EP | 2.2927 | 2.2927 | 2.2927 | 2.2927 | 2.2927 | 0
Bio_Solid_Steam_Turbine_EP | 3.057 | 3.057 | 3.057 | 3.057 | 3.057 | 0
Bio_Solid_Steam_Turbine_Cogen_EP | 2.2927 | 2.2927 | 2.2927 | 2.2927 | 2.2927 | 0

## CPV Cost Calcs
(in 2010 $)
year | $/Wp
2010 | 4.7
2011 | 4.25
2013 | 3.3 | cost declination rate
2015 | 2.6 | -0.062859
2016 | 2.47
2017 | 2.35
2018 | 2.23
2019 | 2.12
2020 | 2.01
2021 | 1.92
2022 | 1.83
2023 | 1.74
2024 | 1.65
2025 | 1.56
2026 | 1.47
2027 | 1.38
2028 | 1.29
2029 | 1.2
2030 | 1.11

## spinning_reserves_penalty
Switch equivalent | Heat rate at percent of full load |  |  |  | 1-min ramp rate | 10-min ramp rate | heat_rate_penalty_spinning_reserve | Note
| 25% | 50% | 75% | 100%
CCGT | 1.788 | 1.195 | 1.102 | 1 | 0.038 | 0.38 | 0.306
Gas_Steam_Turbine | 1.276 | 1.061 | 1.01 | 1 | 0.031 | 0.31 | 0.03
Gas_Combustion_Turbine | 1.504 | 1.095 | 1.029 | 1 | 0.135 | 1 | 0.087 | We assume that a combustion turbine will never run at part load lower than 50 percent, so the 10-min ramp rate used to calculate the heat rate penalty is 0.5 rather than 1.
Sources
Heat rate curve | Structure and Performance of Six European Wholesale Electricity Markets in 2003, 2004, and 2005. Appendix I. DG Comp. Presented to DG Comp 26th February 2007
Ramp rates | WWSIS, p. 174
|  | Part load relative heat rate |  |  | Heat rate penalty |  |  |  | Extra Fuel D | Extra Fuel (Sp)
Percent of full load | Spinning reserve provided | CCGT | Steam | Combustion | CCGT | Steam | Combustion |  | CCGT | CCGT
100% | 0% | 1 | 1 | 1 | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
99% | 1% | 1.0041 | 1.0004 | 1.0012 | 0.40392 | 0.0396 | 0.11484 |  | 0.028274 | 0.028274
98% | 2% | 1.0082 | 1.0008 | 1.0023 | 0.39984 | 0.0392 | 0.11368 |  | 0.055978 | 0.055978
97% | 3% | 1.0122 | 1.0012 | 1.0035 | 0.39576 | 0.0388 | 0.11252 |  | 0.08311 | 0.08311
96% | 4% | 1.0163 | 1.0016 | 1.0046 | 0.39168 | 0.0384 | 0.11136 |  | 0.10967 | 0.10967
95% | 5% | 1.0204 | 1.002 | 1.0058 | 0.3876 | 0.038 | 0.1102 |  | 0.13566 | 0.13566
94% | 6% | 1.0245 | 1.0024 | 1.007 | 0.38352 | 0.0376 | 0.10904 |  | 0.16108 | 0.16108
93% | 7% | 1.0286 | 1.0028 | 1.0081 | 0.37944 | 0.0372 | 0.10788 |  | 0.18593 | 0.18593
92% | 8% | 1.0326 | 1.0032 | 1.0093 | 0.37536 | 0.0368 | 0.10672 |  | 0.2102 | 0.2102
91% | 9% | 1.0367 | 1.0036 | 1.0104 | 0.37128 | 0.0364 | 0.10556 |  | 0.23391 | 0.23391
90% | 10% | 1.0408 | 1.004 | 1.0116 | 0.3672 | 0.036 | 0.1044 |  | 0.25704 | 0.25704
89% | 11% | 1.0449 | 1.0044 | 1.0128 | 0.36312 | 0.0356 | 0.10324 |  | 0.2796 | 0.2796
88% | 12% | 1.049 | 1.0048 | 1.0139 | 0.35904 | 0.0352 | 0.10208 |  | 0.30159 | 0.30159
87% | 13% | 1.053 | 1.0052 | 1.0151 | 0.35496 | 0.0348 | 0.10092 |  | 0.32301 | 0.32301
86% | 14% | 1.0571 | 1.0056 | 1.0162 | 0.35088 | 0.0344 | 0.09976 |  | 0.34386 | 0.34386
85% | 15% | 1.0612 | 1.006 | 1.0174 | 0.3468 | 0.034 | 0.0986 |  | 0.36414 | 0.36414
84% | 16% | 1.0653 | 1.0064 | 1.0186 | 0.34272 | 0.0336 | 0.09744 |  | 0.38385 | 0.38385
83% | 17% | 1.0694 | 1.0068 | 1.0197 | 0.33864 | 0.0332 | 0.09628 |  | 0.40298 | 0.40298
82% | 18% | 1.0734 | 1.0072 | 1.0209 | 0.33456 | 0.0328 | 0.09512 |  | 0.42155 | 0.42155
81% | 19% | 1.0775 | 1.0076 | 1.022 | 0.33048 | 0.0324 | 0.09396 |  | 0.43954 | 0.43954
80% | 20% | 1.0816 | 1.008 | 1.0232 | 0.3264 | 0.032 | 0.0928 |  | 0.45696 | 0.45696
79% | 21% | 1.0857 | 1.0084 | 1.0244 | 0.32232 | 0.0316 | 0.09164 |  | 0.47381 | 0.47381
78% | 22% | 1.0898 | 1.0088 | 1.0255 | 0.31824 | 0.0312 | 0.09048 |  | 0.49009 | 0.49009
77% | 23% | 1.0938 | 1.0092 | 1.0267 | 0.31416 | 0.0308 | 0.08932 |  | 0.5058 | 0.5058
76% | 24% | 1.0979 | 1.0096 | 1.0278 | 0.31008 | 0.0304 | 0.08816 |  | 0.52093 | 0.52093
75% | 25% | 1.102 | 1.01 | 1.029 | 0.306 | 0.03 | 0.087 |  | 0.5355 | 0.5355
74% | 26% | 1.1057 | 1.012 | 1.0316 | 0.3009 | 0.034268 | 0.090052 |  | 0.54763 | 0.54763
73% | 27% | 1.1094 | 1.0141 | 1.0343 | 0.29589 | 0.038068 | 0.092683 |  | 0.55924 | 0.55924
72% | 28% | 1.1132 | 1.0161 | 1.0369 | 0.29098 | 0.041451 | 0.094937 |  | 0.57033 | 0.57033
71% | 29% | 1.1169 | 1.0182 | 1.0396 | 0.28615 | 0.044461 | 0.096854 |  | 0.58089 | 0.58089
70% | 30% | 1.1206 | 1.0202 | 1.0422 | 0.2814 | 0.047133 | 0.098467 |  | 0.59094 | 0.59094
69% | 31% | 1.1243 | 1.0222 | 1.0448 | 0.27671 | 0.049502 | 0.099805 |  | 0.60047 | 0.60047
68% | 32% | 1.128 | 1.0243 | 1.0475 | 0.27209 | 0.051595 | 0.10089 |  | 0.60947 | 0.60947
67% | 33% | 1.1318 | 1.0263 | 1.0501 | 0.26751 | 0.053438 | 0.10176 |  | 0.61795 | 0.61795
66% | 34% | 1.1355 | 1.0284 | 1.0528 | 0.26299 | 0.055052 | 0.10242 |  | 0.62592 | 0.62592
65% | 35% | 1.1392 | 1.0304 | 1.0554 | 0.25851 | 0.056457 | 0.10289 |  | 0.63336 | 0.63336
64% | 36% | 1.1429 | 1.0324 | 1.058 | 0.25408 | 0.057671 | 0.10318 |  | 0.64028 | 0.64028
63% | 37% | 1.1466 | 1.0345 | 1.0607 | 0.24968 | 0.058709 | 0.10332 |  | 0.64668 | 0.64668
62% | 38% | 1.1504 | 1.0365 | 1.0633 | 0.24532 | 0.059585 | 0.10331 |  | 0.65256 | 0.65256
61% | 39% | 1.1541 | 1.0386 | 1.066 | 0.241 | 0.060312 | 0.10317 |  | 0.65792 | 0.65792
60% | 40% | 1.1578 | 1.0406 | 1.0686 | 0.2367 | 0.0609 | 0.1029 |  | 0.66276 | 0.66276
59% | 41% | 1.1615 | 1.0426 | 1.0712 | 0.23243 | 0.06136 | 0.10252 |  | 0.66708 | 0.66708
58% | 42% | 1.1652 | 1.0447 | 1.0739 | 0.22819 | 0.061701 | 0.10202 |  | 0.67087 | 0.67087
57% | 43% | 1.169 | 1.0467 | 1.0765 | 0.22397 | 0.061931 | 0.10143 |  | 0.67415 | 0.67415
56% | 44% | 1.1727 | 1.0488 | 1.0792 | 0.21977 | 0.062058 | 0.10075 |  | 0.67691 | 0.67691
55% | 45% | 1.1764 | 1.0508 | 1.0818 | 0.2156 | 0.062089 | 0.099978 |  | 0.67914 | 0.67914
54% | 46% | 1.1801 | 1.0528 | 1.0844 | 0.21145 | 0.06203 | 0.099125 |  | 0.68085 | 0.68085
53% | 47% | 1.1838 | 1.0549 | 1.0871 | 0.20731 | 0.061886 | 0.098197 |  | 0.68205 | 0.68205
52% | 48% | 1.1876 | 1.0569 | 1.0897 | 0.20319 | 0.061663 | 0.097197 |  | 0.68272 | 0.68272
51% | 49% | 1.1913 | 1.059 | 1.0924 | 0.19909 | 0.061367 | 0.09613 |  | 0.68287 | 0.68287
50% | 50% | 1.195 | 1.061 | 1.095 | 0.195 | 0.061 | 0.095 |  | 0.6825 | 0.6825

## deep_cycling_penalty
Switch equivalent | Heat rate at percent of full load |  |  |  | 1-min ramp rate | 10-min ramp rate | heat_rate_penalty_spinning_reserve | Note
| 25% | 50% | 75% | 100%
CCGT | 1.788 | 1.195 | 1.102 | 1 | 0.038 | 0.38 | 0.306
Gas_Steam_Turbine | 1.276 | 1.061 | 1.01 | 1 | 0.031 | 0.31 | 0.03
Gas_Combustion_Turbine | 1.504 | 1.095 | 1.029 | 1 | 0.135 | 1 | 0.087 | We assume that a combustion turbine will never run at part load lower than 50 percent, so the 10-min ramp rate used to calculate the heat rate penalty is 0.5 rather than 1.
Sources
Heat rate curve | Structure and Performance of Six European Wholesale Electricity Markets in 2003, 2004, and 2005. Appendix I. DG Comp. Presented to DG Comp 26th February 2007
Ramp rates | WWSIS, p. 174
| Part load relative heat rate |  |  | Partial loading penalty |  |  |  | Average penalty up to 40 percent loading
Percent of full load | CCGT | Steam | Combustion | CCGT | Steam | Combustion |  | CCGT | Steam | Combustion
100% | 1 | 1 | 1 | #DIV/0! | #DIV/0! | #DIV/0! |  | 0.29291 | 0.051769 | 0.10767
99% | 1.0041 | 1.0004 | 1.0012 | 0.40392 | 0.0396 | 0.11484
98% | 1.0082 | 1.0008 | 1.0023 | 0.39984 | 0.0392 | 0.11368
97% | 1.0122 | 1.0012 | 1.0035 | 0.39576 | 0.0388 | 0.11252
96% | 1.0163 | 1.0016 | 1.0046 | 0.39168 | 0.0384 | 0.11136
95% | 1.0204 | 1.002 | 1.0058 | 0.3876 | 0.038 | 0.1102
94% | 1.0245 | 1.0024 | 1.007 | 0.38352 | 0.0376 | 0.10904
93% | 1.0286 | 1.0028 | 1.0081 | 0.37944 | 0.0372 | 0.10788
92% | 1.0326 | 1.0032 | 1.0093 | 0.37536 | 0.0368 | 0.10672
91% | 1.0367 | 1.0036 | 1.0104 | 0.37128 | 0.0364 | 0.10556
90% | 1.0408 | 1.004 | 1.0116 | 0.3672 | 0.036 | 0.1044
89% | 1.0449 | 1.0044 | 1.0128 | 0.36312 | 0.0356 | 0.10324
88% | 1.049 | 1.0048 | 1.0139 | 0.35904 | 0.0352 | 0.10208
87% | 1.053 | 1.0052 | 1.0151 | 0.35496 | 0.0348 | 0.10092
86% | 1.0571 | 1.0056 | 1.0162 | 0.35088 | 0.0344 | 0.09976
85% | 1.0612 | 1.006 | 1.0174 | 0.3468 | 0.034 | 0.0986
84% | 1.0653 | 1.0064 | 1.0186 | 0.34272 | 0.0336 | 0.09744
83% | 1.0694 | 1.0068 | 1.0197 | 0.33864 | 0.0332 | 0.09628
82% | 1.0734 | 1.0072 | 1.0209 | 0.33456 | 0.0328 | 0.09512
81% | 1.0775 | 1.0076 | 1.022 | 0.33048 | 0.0324 | 0.09396
80% | 1.0816 | 1.008 | 1.0232 | 0.3264 | 0.032 | 0.0928
79% | 1.0857 | 1.0084 | 1.0244 | 0.32232 | 0.0316 | 0.09164
78% | 1.0898 | 1.0088 | 1.0255 | 0.31824 | 0.0312 | 0.09048
77% | 1.0938 | 1.0092 | 1.0267 | 0.31416 | 0.0308 | 0.08932
76% | 1.0979 | 1.0096 | 1.0278 | 0.31008 | 0.0304 | 0.08816
75% | 1.102 | 1.01 | 1.029 | 0.306 | 0.03 | 0.087
74% | 1.1057 | 1.012 | 1.0316 | 0.3009 | 0.034268 | 0.090052
73% | 1.1094 | 1.0141 | 1.0343 | 0.29589 | 0.038068 | 0.092683
72% | 1.1132 | 1.0161 | 1.0369 | 0.29098 | 0.041451 | 0.094937
71% | 1.1169 | 1.0182 | 1.0396 | 0.28615 | 0.044461 | 0.096854
70% | 1.1206 | 1.0202 | 1.0422 | 0.2814 | 0.047133 | 0.098467
69% | 1.1243 | 1.0222 | 1.0448 | 0.27671 | 0.049502 | 0.099805
68% | 1.128 | 1.0243 | 1.0475 | 0.27209 | 0.051595 | 0.10089
67% | 1.1318 | 1.0263 | 1.0501 | 0.26751 | 0.053438 | 0.10176
66% | 1.1355 | 1.0284 | 1.0528 | 0.26299 | 0.055052 | 0.10242
65% | 1.1392 | 1.0304 | 1.0554 | 0.25851 | 0.056457 | 0.10289
64% | 1.1429 | 1.0324 | 1.058 | 0.25408 | 0.057671 | 0.10318
63% | 1.1466 | 1.0345 | 1.0607 | 0.24968 | 0.058709 | 0.10332
62% | 1.1504 | 1.0365 | 1.0633 | 0.24532 | 0.059585 | 0.10331
61% | 1.1541 | 1.0386 | 1.066 | 0.241 | 0.060312 | 0.10317
60% | 1.1578 | 1.0406 | 1.0686 | 0.2367 | 0.0609 | 0.1029
59% | 1.1615 | 1.0426 | 1.0712 | 0.23243 | 0.06136 | 0.10252
58% | 1.1652 | 1.0447 | 1.0739 | 0.22819 | 0.061701 | 0.10202
57% | 1.169 | 1.0467 | 1.0765 | 0.22397 | 0.061931 | 0.10143
56% | 1.1727 | 1.0488 | 1.0792 | 0.21977 | 0.062058 | 0.10075 |  |  |  | The penalty factor applied is calculated as follows:
55% | 1.1764 | 1.0508 | 1.0818 | 0.2156 | 0.062089 | 0.099978
54% | 1.1801 | 1.0528 | 1.0844 | 0.21145 | 0.06203 | 0.099125 |  |  |  | Fuel use as represented by SWITCH = Actual fuel use
53% | 1.1838 | 1.0549 | 1.0871 | 0.20731 | 0.061886 | 0.098197 |  |  |  | DispatchGen x heat_rate + (Installed_Capacity – DispatchGen) x penalty x heat_rate = DispatchGen x degraded_heat_rate
52% | 1.1876 | 1.0569 | 1.0897 | 0.20319 | 0.061663 | 0.097197
51% | 1.1913 | 1.059 | 1.0924 | 0.19909 | 0.061367 | 0.09613 |  |  |  | Normalizing for installed capacity, this gives us:
50% | 1.195 | 1.061 | 1.095 | 0.195 | 0.061 | 0.095
49% | 1.2183 | 1.0696 | 1.1114 | 0.20976 | 0.066871 | 0.10699 |  |  |  | ( DispatchGen x heat_rate + (Installed_Capacity – DispatchGen) x penalty x heat_rate) / Installed_Capacity = DispatchGen x degraded_heat_rate / Installed_Capacity
48% | 1.2416 | 1.0782 | 1.1277 | 0.22305 | 0.072185 | 0.1179
47% | 1.265 | 1.0868 | 1.1441 | 0.23496 | 0.076974 | 0.12777 |  |  |  | fraction_dispatched x heat_rate + (1 – fraction_dispatched) x penalty x heat_rate = fraction_dispatched x degraded_heat_rate
46% | 1.2883 | 1.0954 | 1.1604 | 0.24557 | 0.081267 | 0.13667
45% | 1.3116 | 1.104 | 1.1768 | 0.25495 | 0.085091 | 0.14465 |  |  |  | penalty = ( fraction_dispatched x (degraded_heat_rate – heat_rate ) ) / ( (1 – fraction_dispatched ) x heat_rate )
44% | 1.3349 | 1.1126 | 1.1932 | 0.26315 | 0.088471 | 0.15177
43% | 1.3582 | 1.1212 | 1.2095 | 0.27025 | 0.091432 | 0.15806
42% | 1.3816 | 1.1298 | 1.2259 | 0.2763 | 0.093993 | 0.16357
41% | 1.4049 | 1.1384 | 1.2422 | 0.28136 | 0.096176 | 0.16834
40% | 1.4282 | 1.147 | 1.2586 | 0.28547 | 0.098 | 0.1724
39% | 1.4515 | 1.1556 | 1.275 | 0.28868 | 0.099482 | 0.17579
38% | 1.4748 | 1.1642 | 1.2913 | 0.29103 | 0.10064 | 0.17855
37% | 1.4982 | 1.1728 | 1.3077 | 0.29257 | 0.10149 | 0.1807
36% | 1.5215 | 1.1814 | 1.324 | 0.29333 | 0.10204 | 0.18227
35% | 1.5448 | 1.19 | 1.3404 | 0.29335 | 0.10231 | 0.18329
34% | 1.5681 | 1.1986 | 1.3568 | 0.29267 | 0.10231 | 0.18379
33% | 1.5914 | 1.2072 | 1.3731 | 0.29131 | 0.10205 | 0.18378
32% | 1.6148 | 1.2158 | 1.3895 | 0.2893 | 0.10155 | 0.18328
31% | 1.6381 | 1.2244 | 1.4058 | 0.28667 | 0.10082 | 0.18233
30% | 1.6614 | 1.233 | 1.4222 | 0.28346 | 0.099857 | 0.18094
29% | 1.6847 | 1.2416 | 1.4386 | 0.27967 | 0.098682 | 0.17913
28% | 1.708 | 1.2502 | 1.4549 | 0.27535 | 0.0973 | 0.17691
27% | 1.7314 | 1.2588 | 1.4713 | 0.2705 | 0.095721 | 0.17431
26% | 1.7547 | 1.2674 | 1.4876 | 0.26516 | 0.093951 | 0.17133
25% | 1.778 | 1.276 | 1.504 | 0.25933 | 0.092 | 0.168