## generator_costs
note: we assume that cogen plants have 3/4 of the capital cost of a pure-electric plant, (to reflect shared infrastructure for cogen), but the same operating costs.
technology_id | technology | price_and_dollar_year | min_build_year | fuel | $year_of_costs | interest_between_price_year_and_cost_year | cost_for_which_year? | overnight_cost | construction_cost_multipulier | fixed_o_m | var_o_m | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | overnight_cost_change | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | baseload | dispatchable | cogen | min_build_capacity | can_build_new | ccs | storage | storage_efficiency | max_store_rate | tech_name_again | source - all dispatch data from TEPPC_Generator_Categories
1 | CCGT | 2007 | 2010 | Gas | 2004 | 1.098 | 2010 | 896906 | 1.07 | 11013 | 1.8537 | 1097594.1366 | 12092.274 | 2.0353 | -0.0135 | 91289 | 6.974 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | CCGT | ReEDs Sheet
2 | Gas_Combustion_Turbine | 2007 | 2010 | Gas | 2004 | 1.098 | 2010 | 593905 | 1.04 | 10311 | 3.0515 | 708354.3684 | 11321.478 | 3.3505 | -0.0144 | 91289 | 10.05 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Gas_Combustion_Turbine | ReEDs Sheet
3 | Concentrating_PV | 2007 | 2010 | Solar | 2010 | 0.965 | 2010 | 4700000 | 1.05 | 17000 | 0 | 5786275.8115 | 16405 | 0 | -0.062859 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 25 | 0.0027 | 0.0054 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Concentrating_PV | CPV Consortium numbers (It's more or less SolFocus)
4 | Wind | 2007 | 2010 | Wind | 2004 | 1.098 | 2010 | 1596000 | 1.05 | 52633 | 0 | 1867907.1477 | 57791.034 | 0 | -0.005 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 20 | 0.015 | 0.003 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Wind | Black and Veatch for REFutures (12-02-09 update) (onReEDs sheet) for capital cost, outage rates from Mathias
5 | Offshore_Wind | 2007 | 2010 | Wind | 2004 | 1.098 | 2010 | 2833000 | 1.13 | 87721 | 0 | 3655745.0457 | 96317.658 | 0 | -0.013 | 65639 | 0 | 4 | 0.7 | 0.1 | 0.1 | 0.1 | 0 | 0 | 20 | 0.02 | 0.01 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Offshore_Wind | Black and Veatch for REFutures (12-02-09 update) (onReEDs sheet) for capital cost, EIA says minimum learning by 2025 is 20%, so this is a 1.1% declination rate, capital cost multipulier from EIA,http://graysharboroceanenergy.com/Documents/LIPA%20Offshore%20Wind%20rept.pdf for total outage rate of 3%, distributed by guess
6 | Residential_PV | 2007 | 2010 | Solar | 2009 | 0.97 | 2010 | 5950000 | 1.05 | 10526 | 0 | 7034797.834 | 10210.22 | 0 | -0.0485 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Residential_PV | DOE Solar Program Costs, took 2020 value for fixed O+M, 10% added to capital costs to go from utility to distributed, but also assumed a 5% declination rate, , outage rates from Mathias
7 | CSP_Trough_6h_Storage | 2007 | 2012 | Solar | 2010 | 0.965 | 2010 | 6821000 | 1.05 | 49906 | 0 | 7098171.7915 | 48159.29 | 0 | -0.00885 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | CSP_Trough_6h_Storage | CapEx from SAM with Solar Field area = 800000m^2 and 6h TES, construction cost mulitplier and yearly cost fraction from CSP on ReEDs sheet- it's unclear how much these change with storage... assumed to be the same here, cost declination rate and fixed OM from Black and Veach ReEDs sheet. Most places put VarOM at 0, so this was done here
8 | Bio_Gas | 2007 | 2010 | Bio_Gas | 2007 | 1 | 2008 | 2377000 | 1.07 | 114250 | 0.01 | 2580549.9188 | 114250 | 0.01 | -0.0144 | 91289 | 13.648 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Bio_Gas | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to gas combustion turbine
9 | Biomass_Steam_Turbine | 2007 | 2010 | Bio_Solid | 2004 | 1.098 | 2010 | 2617450 | 1.1 | 66626 | 9.518 | 3214097.5754 | 73155.348 | 10.4508 | -0.0055 | 91289 | 14.5 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.09 | 0.076 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Biomass_Steam_Turbine | ReEDs Sheet, cost declination rate assumed to be that of a gas steam turbine
10 | Biomass_IGCC | 2007 | 2012 | Bio_Solid | 2007 | 1 | 2008 | 3339000 | 1.12 | 64450 | 6.71 | 3795858.7089 | 64450 | 6.71 | -0.0148 | 91289 | 9.646 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Biomass_IGCC | EIA, cost declination rate, construction time, lifetime, outage rates assumed to be equal to coal IGCC
11 | Coal_IGCC | 2007 | 2010 | Coal | 2004 | 1.098 | 2010 | 2166113 | 1.17 | 35224 | 2.6598 | 2910020.8532 | 38675.952 | 2.9205 | -0.0148 | 91289 | 8.765 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Coal_IGCC | ReEDs Sheet, assumed to run for 40 years, not 60
12 | Coal_Steam_Turbine | 2007 | 2010 | Coal | 2004 | 1.098 | 2010 | 1874626 | 1.1 | 25077 | 4.181 | 2346966.894 | 27534.546 | 4.5908 | -0.0119 | 91289 | 9.2 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Coal_Steam_Turbine | ReEDs Sheet, assumed to run for 40 years, not 60
13 | Nuclear | 2007 | 2010 | Uranium | 2004 | 1.098 | 2010 | 3022356 | 1.2 | 81999 | 0.44634 | 3982256.2656 | 90034.902 | 0.49008 | 0 | 91289 | 10.434 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 40 | 0.04 | 0.06 | 0 | 0 | 1 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0 | Nuclear | ReEDs Sheet, nukes run for 40 years at least, so the 30 year ReEDs lifetime was changed to 40, also the cost declination rate was set to 0.55% as nukes don't really obey the laws of mass production because they aren't mass produced
14 | Geothermal | 2007 | 2010 | Geothermal | 2004 | 1.098 | 2010 | 3039350 | 1.1 | 237950 | 0 | 3783294.5618 | 261269.1 | 0 | -0.01 | 65639 | 32.32 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.0075 | 0.0241 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Geothermal | ReEDs Sheet, cost declination rate assumed to be between ST and other techs (@1%). EIA has minimum learning by 2025 as 10%, so this is roughly consistent
15 | Hydro_NonPumped | 2007 | 2010 | Water | 2007 | 1 | 2000 | 2242369 | 1 | 13632 | 2.43 | 2242369 | 13632 | 2.43 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 100 | 0.05 | 0.019 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hydro_NonPumped | ReEDs Sheet
16 | Hydro_Pumped | 2007 | 2010 | Water | 2007 | 1 | 2000 | 3860420 | 1 | 29666 | 0 | 3860420 | 29666 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 100 | 0.038 | 0.03 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1 | Hydro_Pumped | ReEDs Sheet, storage effiency from Samir Succar and Robert H. Williams: Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power, p. 39
17 | Gas_Combustion_Turbine_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 652000 | 1 | 11322 | 3.35 | 652000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Combustion_Turbine_EP | ReEDs Sheet
18 | Coal_Steam_Turbine_EP | 2007 | 2000 | Coal | 2007 | 1 | 2000 | 1322000 | 1 | 25703 | 3.73 | 1322000 | 25703 | 3.73 | 0 | 0 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coal_Steam_Turbine_EP | ReEDs Sheet, took CoalOldScr costs
19 | Gas_Steam_Turbine_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 435000 | 1 | 27730 | 3.47 | 435000 | 27730 | 3.47 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Steam_Turbine_EP | ReEDs Sheet, took OGS (Oil Gas Steam)
20 | CCGT_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 955000 | 1 | 11322 | 3.35 | 955000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CCGT_EP | ReEDs Sheet
21 | Geothermal_EP | 2007 | 2000 | Geothermal | 2007 | 1 | 2000 | 3397000 | 1 | 261269 | 0 | 3397000 | 261269 | 0 | 0 | 0 | 0 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.075 | 0.0241 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Geothermal_EP | ReEDs Sheet
22 | Nuclear_EP | 2007 | 2000 | Uranium | 2007 | 1 | 2000 | 3319000 | 1 | 90034 | 0.49 | 3319000 | 90034 | 0.49 | 0 | 0 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 60 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Nuclear_EP | ReEDs Sheet, set lifetime to 60 years
23 | Wind_EP | 2007 | 2000 | Wind | 2007 | 1 | 2000 | 1724000 | 1 | 57790 | 0 | 1724000 | 57790 | 0 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.015 | 0.003 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wind_EP | ReEDs Sheet, also new wind params used for fixed O+M, forced outage rate
24 | Gas_Internal_Combustion_Engine_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 652000 | 1 | 30000 | 1 | 652000 | 30000 | 1 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Internal_Combustion_Engine_EP | ReEDs Sheet
25 | Commercial_PV | 2007 | 2010 | Solar | 2009 | 0.97 | 2010 | 5100000 | 1.05 | 10526 | 0 | 5976906.1693 | 10210.22 | 0 | -0.0457 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Commercial_PV | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, ReEDs sheet for construction cost multiplier and cost fractions, Matthias for forced outage rate
26 | Central_PV | 2007 | 2010 | Solar | 2009 | 0.97 | 2010 | 4060000 | 1.05 | 10526 | 0 | 4634620.2138 | 10210.22 | 0 | -0.0373 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Central_PV | Solar Vision Study (see PV_Cost_Calc.xlsx) for costs, ReEDs sheet for construction cost multiplier and cost fractions, Matthias for forced outage rate
27 | CSP_Trough_No_Storage | 2007 | 2010 | Solar | 2010 | 0.965 | 2010 | 4230000 | 1.05 | 49906 | 0 | 4401886.3331 | 48159.29 | 0 | -0.00885 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | CSP_Trough_No_Storage | CapEx from SAM with Solar Field area = 600000m^2, construction cost mulitplier and yearly cost fraction from ReEDs sheet, cost declination rate and fixed OM from Black and Veach on ReEDs sheet. Most places put VarOM at 0, so this was done here
28 | Compressed_Air_Energy_Storage | 2007 | 2010 | Gas | 2010 | 0.965 | 2010 | 1200000 | 1.2068 | 10310 | 3.1 | 1402503.9775 | 9949.15 | 2.9915 | -0.0012 | 91289 | 4.4 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0.817 | 1.2 | Compressed_Air_Energy_Storage | ReEDs Sheet; also Sullivan et al (2008), NREL/CP-670-43510 Conference Paper for o&m costs, declanation rate, etc; $1,200,000 taken as capital cost in 2010 rather than 2004 based on conversation with Hernandez, also The storage efficiency of the the storage phase of compressed air energy storage from Samir Succar and Robert H. Williams: Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power, p. 39
29 | Gas_Combustion_Turbine_Cogen_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 489000 | 1 | 11322 | 3.35 | 489000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Combustion_Turbine_Cogen_EP | ReEDs Sheet, 75 CapEx of non-cogen
30 | Coal_Steam_Turbine_Cogen_EP | 2007 | 2000 | Coal | 2007 | 1 | 2000 | 991500 | 1 | 25703 | 3.73 | 991500 | 25703 | 3.73 | 0 | 0 | 0 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Coal_Steam_Turbine_Cogen_EP | ReEDs Sheet, 75 CapEx of non-cogen
31 | Gas_Steam_Turbine_Cogen_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 326250 | 1 | 27730 | 3.47 | 326250 | 27730 | 3.47 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Steam_Turbine_Cogen_EP | ReEDs Sheet, 75 CapEx of non-cogen
32 | CCGT_Cogen_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 716250 | 1 | 11322 | 3.35 | 716250 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | CCGT_Cogen_EP | ReEDs Sheet, 75 CapEx of non-cogen
33 | Battery_Storage | 2007 | 2010 | Storage | 2004 | 1.098 | 2010 | 3539000 | 1.049 | 22100 | 0.445 | 4144936.7381 | 24265.8 | 0.48861 | -0.0055564 | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 15 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.767 | 1 | Battery_Storage | ReEDs Sheet
34 | CCGT_CCS | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 3191692 | 1.07 | 18127 | 2.6777 | 3961894.0068 | 19903.446 | 2.9401 | -0.018174 | 91289 | 10.004 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | CCGT_CCS | ReEDs Sheet
35 | Gas_Combustion_Turbine_CCS | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2888691 | 1.04 | 17425 | 3.8755 | 3494840.6211 | 19132.65 | 4.2553 | -0.019074 | 91289 | 13.08 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_CCS | ReEDs Sheet
36 | Bio_Gas_CCS | 2007 | 2014 | Bio_Gas_CCS | 2004 | 1.098 | 2010 | 4671786 | 1.07 | 121364 | 0.834 | 5815133.1845 | 133257.672 | 0.91573 | -0.019074 | 91289 | 16.678 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Bio_Gas_CCS | ReEDs Sheet
37 | Biomass_IGCC_CCS | 2007 | 2014 | Bio_Solid_CCS | 2004 | 1.098 | 2010 | 5633786 | 1.12 | 71236 | 8.095 | 7294966.6908 | 78217.128 | 8.8883 | -0.017048 | 91289 | 11.782 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Biomass_IGCC_CCS | ReEDs Sheet
38 | Coal_IGCC_CCS | 2007 | 2014 | Coal_CCS | 2004 | 1.098 | 2010 | 4460899 | 1.17 | 42010 | 4.0448 | 6034109.6319 | 46126.98 | 4.4412 | -0.017048 | 91289 | 9.099 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Coal_IGCC_CCS | ReEDs Sheet
39 | Coal_Steam_Turbine_CCS | 2007 | 2014 | Coal_CCS | 2004 | 1.098 | 2010 | 4169412 | 1.1 | 31863 | 5.566 | 5255744.0747 | 34985.574 | 6.1115 | -0.014148 | 91289 | 11.336 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_CCS | ReEDs Sheet
40 | Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 2000 | Gas | 2007 | 1 | 2000 | 489000 | 1 | 30000 | 1 | 489000 | 30000 | 1 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.04 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Gas_Internal_Combustion_Engine_Cogen_EP | ReEDs Sheet, 75 CapEx of non-cogen
41 | Gas_Combustion_Turbine_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 18436 | 4.174 | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_EP | ReEDs Sheet
42 | Coal_Steam_Turbine_CCS_EP | 2007 | 2014 | Coal_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 32489 | 5.115 | 2790415.9072 | 35672.922 | 5.6163 | -0.0022477 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_EP | ReEDs Sheet
43 | Gas_Steam_Turbine_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 34516 | 4.855 | 2810868.4743 | 37898.568 | 5.3308 | -0.0046735 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Gas_Steam_Turbine_EP | ReEDs Sheet
44 | CCGT_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 18436 | 4.174 | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | CCGT_EP | ReEDs Sheet
45 | Gas_Combustion_Turbine_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 18436 | 4.174 | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_Cogen_EP | ReEDs Sheet
46 | Coal_Steam_Turbine_Cogen_CCS_EP | 2007 | 2014 | Coal_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 32489 | 5.115 | 2790415.9072 | 35672.922 | 5.6163 | -0.0022477 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_Cogen_EP | ReEDs Sheet
47 | Gas_Steam_Turbine_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 34516 | 4.855 | 2810868.4743 | 37898.568 | 5.3308 | -0.0046735 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Gas_Steam_Turbine_Cogen_EP | ReEDs Sheet
48 | CCGT_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2004 | 1.098 | 2010 | 2294786 | 1.1 | 18436 | 4.174 | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | CCGT_Cogen_EP | ReEDs Sheet

## Cost CSV For Export
technology_id | technology | price_and_dollar_year | min_build_year | fuel | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | overnight_cost_change | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | resource_limited | baseload | dispatchable | cogen | min_build_capacity | can_build_new | ccs | storage | storage_efficiency | max_store_rate
1 | CCGT | 2007 | 2010 | Gas | 1097594.1366 | 12092.274 | 2.0353 | -0.0135 | 91289 | 6.974 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | Gas_Combustion_Turbine | 2007 | 2010 | Gas | 708354.3684 | 11321.478 | 3.3505 | -0.0144 | 91289 | 10.05 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
3 | Concentrating_PV | 2007 | 2010 | Solar | 5786275.8115 | 16405 | 0 | -0.062859 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 25 | 0.0027 | 0.0054 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
4 | Wind | 2007 | 2010 | Wind | 1867907.1477 | 57791.034 | 0 | -0.005 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 20 | 0.015 | 0.003 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
5 | Offshore_Wind | 2007 | 2010 | Wind | 3655745.0457 | 96317.658 | 0 | -0.013 | 65639 | 0 | 4 | 0.7 | 0.1 | 0.1 | 0.1 | 0 | 0 | 20 | 0.02 | 0.01 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
6 | Residential_PV | 2007 | 2010 | Solar | 7034797.834 | 10210.22 | 0 | -0.0485 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
7 | CSP_Trough_6h_Storage | 2007 | 2012 | Solar | 7098171.7915 | 48159.29 | 0 | -0.00885 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
8 | Bio_Gas | 2007 | 2010 | Bio_Gas | 2580549.9188 | 114250 | 0.01 | -0.0144 | 91289 | 13.648 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
9 | Biomass_Steam_Turbine | 2007 | 2010 | Bio_Solid | 3214097.5754 | 73155.348 | 10.4508 | -0.0055 | 91289 | 14.5 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.09 | 0.076 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
10 | Biomass_IGCC | 2007 | 2012 | Bio_Solid | 3795858.7089 | 64450 | 6.71 | -0.0148 | 91289 | 9.646 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
11 | Coal_IGCC | 2007 | 2010 | Coal | 2910020.8532 | 38675.952 | 2.9205 | -0.0148 | 91289 | 8.765 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
12 | Coal_Steam_Turbine | 2007 | 2010 | Coal | 2346966.894 | 27534.546 | 4.5908 | -0.0119 | 91289 | 9.2 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
13 | Nuclear | 2007 | 2010 | Uranium | 3982256.2656 | 90034.902 | 0.49008 | 0 | 91289 | 10.434 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 40 | 0.04 | 0.06 | 0 | 0 | 1 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0
14 | Geothermal | 2007 | 2010 | Geothermal | 3783294.5618 | 261269.1 | 0 | -0.01 | 65639 | 32.32 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.0075 | 0.0241 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
15 | Hydro_NonPumped | 2007 | 2010 | Water | 2242369 | 13632 | 2.43 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 100 | 0.05 | 0.019 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Hydro_Pumped | 2007 | 2010 | Water | 3860420 | 29666 | 0 | 0 | 65639 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 100 | 0.038 | 0.03 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1
17 | Gas_Combustion_Turbine_EP | 2007 | 2000 | Gas | 652000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Coal_Steam_Turbine_EP | 2007 | 2000 | Coal | 1322000 | 25703 | 3.73 | 0 | 0 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Gas_Steam_Turbine_EP | 2007 | 2000 | Gas | 435000 | 27730 | 3.47 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | CCGT_EP | 2007 | 2000 | Gas | 955000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Geothermal_EP | 2007 | 2000 | Geothermal | 3397000 | 261269 | 0 | 0 | 0 | 0 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 45 | 0.075 | 0.0241 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Nuclear_EP | 2007 | 2000 | Uranium | 3319000 | 90034 | 0.49 | 0 | 0 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 60 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | Wind_EP | 2007 | 2000 | Wind | 1724000 | 57790 | 0 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.015 | 0.003 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Gas_Internal_Combustion_Engine_EP | 2007 | 2000 | Gas | 652000 | 30000 | 1 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Commercial_PV | 2007 | 2010 | Solar | 5976906.1693 | 10210.22 | 0 | -0.0457 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
26 | Central_PV | 2007 | 2010 | Solar | 4634620.2138 | 10210.22 | 0 | -0.0373 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.003 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
27 | CSP_Trough_No_Storage | 2007 | 2010 | Solar | 4401886.3331 | 48159.29 | 0 | -0.00885 | 65639 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.05 | 0.05 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
28 | Compressed_Air_Energy_Storage | 2007 | 2010 | Gas | 1402503.9775 | 9949.15 | 2.9915 | -0.0012 | 91289 | 4.4 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0.817 | 1.2
29 | Gas_Combustion_Turbine_Cogen_EP | 2007 | 2000 | Gas | 489000 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
30 | Coal_Steam_Turbine_Cogen_EP | 2007 | 2000 | Coal | 991500 | 25703 | 3.73 | 0 | 0 | 0 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
31 | Gas_Steam_Turbine_Cogen_EP | 2007 | 2000 | Gas | 326250 | 27730 | 3.47 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
32 | CCGT_Cogen_EP | 2007 | 2000 | Gas | 716250 | 11322 | 3.35 | 0 | 0 | 0 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
33 | Battery_Storage | 2007 | 2010 | Storage | 4144936.7381 | 24265.8 | 0.48861 | -0.0055564 | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 15 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.767 | 1
34 | CCGT_CCS | 2007 | 2014 | Gas_CCS | 3961894.0068 | 19903.446 | 2.9401 | -0.018174 | 91289 | 10.004 | 3 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0
35 | Gas_Combustion_Turbine_CCS | 2007 | 2014 | Gas_CCS | 3494840.6211 | 19132.65 | 4.2553 | -0.019074 | 91289 | 13.08 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0
36 | Bio_Gas_CCS | 2007 | 2014 | Bio_Gas_CCS | 5815133.1845 | 133257.672 | 0.91573 | -0.019074 | 91289 | 16.678 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
37 | Biomass_IGCC_CCS | 2007 | 2014 | Bio_Solid_CCS | 7294966.6908 | 78217.128 | 8.8883 | -0.017048 | 91289 | 11.782 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
38 | Coal_IGCC_CCS | 2007 | 2014 | Coal_CCS | 6034109.6319 | 46126.98 | 4.4412 | -0.017048 | 91289 | 9.099 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
39 | Coal_Steam_Turbine_CCS | 2007 | 2014 | Coal_CCS | 5255744.0747 | 34985.574 | 6.1115 | -0.014148 | 91289 | 11.336 | 4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
40 | Gas_Internal_Combustion_Engine_Cogen_EP | 2007 | 2000 | Gas | 489000 | 30000 | 1 | 0 | 0 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.04 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
41 | Gas_Combustion_Turbine_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0
42 | Coal_Steam_Turbine_CCS_EP | 2007 | 2014 | Coal_CCS | 2790415.9072 | 35672.922 | 5.6163 | -0.0022477 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
43 | Gas_Steam_Turbine_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 37898.568 | 5.3308 | -0.0046735 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0
44 | CCGT_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0
45 | Gas_Combustion_Turbine_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.03 | 0.05 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
46 | Coal_Steam_Turbine_Cogen_CCS_EP | 2007 | 2014 | Coal_CCS | 2790415.9072 | 35672.922 | 5.6163 | -0.0022477 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 60 | 0.06 | 0.1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
47 | Gas_Steam_Turbine_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 37898.568 | 5.3308 | -0.0046735 | 0 | 2.136 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 45 | 0.1 | 0.026 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0
48 | CCGT_Cogen_CCS_EP | 2007 | 2014 | Gas_CCS | 2810868.4743 | 20242.728 | 4.5831 | -0.0046735 | 0 | 3.03 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 30 | 0.04 | 0.06 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0

## costs_by_investment_period
Resultant Capital Costs ($2007/MW) in Investment Period Years
technology | 2010 | 2014 | 2018 | 2022 | 2026 | Cost Declination Rate (%/yr)
CCGT | 1.0537 | 0.99798 | 0.94517 | 0.89515 | 0.84779 | 1.35
Gas_Combustion_Turbine | 0.67819 | 0.63996 | 0.60389 | 0.56985 | 0.53773 | 1.44
Concentrating_PV | 4.7623 | 3.6731 | 2.8331 | 2.1851 | 1.6854 | 6.2859
Wind | 1.84 | 1.8035 | 1.7677 | 1.7326 | 1.6982 | 0.5
Offshore_Wind | 3.515 | 3.3358 | 3.1657 | 3.0042 | 2.851 | 1.3
Residential_PV | 6.0601 | 4.9672 | 4.0714 | 3.3372 | 2.7354 | 4.85
CSP_Trough_6h_Storage | 6.9114 | 6.6699 | 6.4369 | 6.2121 | 5.9951 | 0.885
Bio_Gas | 2.4707 | 2.3314 | 2.2 | 2.076 | 1.959 | 1.44
Biomass_Steam_Turbine | 3.1614 | 3.0924 | 3.0249 | 2.9589 | 2.8943 | 0.55
Biomass_IGCC | 3.6298 | 3.4196 | 3.2217 | 3.0351 | 2.8594 | 1.48
Coal_IGCC | 2.7827 | 2.6216 | 2.4698 | 2.3268 | 2.1921 | 1.48
Coal_Steam_Turbine | 2.2642 | 2.1583 | 2.0574 | 1.9612 | 1.8695 | 1.19
Nuclear | 3.9823 | 3.9823 | 3.9823 | 3.9823 | 3.9823 | 0
Geothermal | 3.6709 | 3.5263 | 3.3873 | 3.2539 | 3.1256 | 1
Hydro_NonPumped | 2.2424 | 2.2424 | 2.2424 | 2.2424 | 2.2424 | 0
Hydro_Pumped | 3.8604 | 3.8604 | 3.8604 | 3.8604 | 3.8604 | 0
Gas_Combustion_Turbine_EP | 0.652 | 0.652 | 0.652 | 0.652 | 0.652 | 0
Coal_Steam_Turbine_EP | 1.322 | 1.322 | 1.322 | 1.322 | 1.322 | 0
Gas_Steam_Turbine_EP | 0.435 | 0.435 | 0.435 | 0.435 | 0.435 | 0
CCGT_EP | 0.955 | 0.955 | 0.955 | 0.955 | 0.955 | 0
Geothermal_EP | 3.397 | 3.397 | 3.397 | 3.397 | 3.397 | 0
Nuclear_EP | 3.319 | 3.319 | 3.319 | 3.319 | 3.319 | 0
Wind_EP | 1.724 | 1.724 | 1.724 | 1.724 | 1.724 | 0
Gas_Internal_Combustion_Engine_EP | 0.652 | 0.652 | 0.652 | 0.652 | 0.652 | 0
Commercial_PV | 5.1944 | 4.308 | 3.5728 | 2.9631 | 2.4575 | 4.57
Central_PV | 4.1351 | 3.5518 | 3.0508 | 2.6205 | 2.2508 | 3.73
CSP_Trough_No_Storage | 4.286 | 4.1363 | 3.9918 | 3.8524 | 3.7178 | 0.885
Compressed_Air_Energy_Storage | 1.3975 | 1.3908 | 1.3841 | 1.3775 | 1.3709 | 0.12
Gas_Combustion_Turbine_Cogen_EP | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0
Coal_Steam_Turbine_Cogen_EP | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0.9915 | 0
Gas_Steam_Turbine_Cogen_EP | 0.32625 | 0.32625 | 0.32625 | 0.32625 | 0.32625 | 0
CCGT_Cogen_EP | 0.71625 | 0.71625 | 0.71625 | 0.71625 | 0.71625 | 0
Battery_Storage | 4.0762 | 3.9864 | 3.8985 | 3.8126 | 3.7286 | 0.55564
CCGT_CCS | 3.7498 | 3.4845 | 3.2381 | 3.009 | 2.7962 | 1.8174
Gas_Combustion_Turbine_CCS | 3.2987 | 3.0541 | 2.8277 | 2.618 | 2.4239 | 1.9074
Bio_Gas_CCS | 5.4887 | 5.0818 | 4.705 | 4.3562 | 4.0332 | 1.9074
Biomass_IGCC_CCS | 6.9282 | 6.4677 | 6.0378 | 5.6365 | 5.2619 | 1.7048
Coal_IGCC_CCS | 5.7307 | 5.3498 | 4.9943 | 4.6623 | 4.3524 | 1.7048
Coal_Steam_Turbine_CCS | 5.0358 | 4.7568 | 4.4933 | 4.2444 | 4.0092 | 1.4148
Gas_Internal_Combustion_Engine_Cogen_EP | 0.489 | 0.489 | 0.489 | 0.489 | 0.489 | 0
Gas_Combustion_Turbine_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735
Coal_Steam_Turbine_CCS_EP | 2.7716 | 2.7468 | 2.7222 | 2.6978 | 2.6736 | 0.22477
Gas_Steam_Turbine_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735
CCGT_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735
Gas_Combustion_Turbine_Cogen_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735
Coal_Steam_Turbine_Cogen_CCS_EP | 2.7716 | 2.7468 | 2.7222 | 2.6978 | 2.6736 | 0.22477
Gas_Steam_Turbine_Cogen_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735
CCGT_Cogen_CCS_EP | 2.7716 | 2.7202 | 2.6697 | 2.6201 | 2.5715 | 0.46735

## CPV Cost Calcs
(in 2010 $)
year | $/Wp
2010 | 4.7
2011 | 4.25
2013 | 3.3 | cost declination rate
2015 | 2.6 | -0.062859
2016 | 2.47
2017 | 2.35
2018 | 2.23
2019 | 2.12
2020 | 2.01
2021 | 1.92
2022 | 1.83
2023 | 1.74
2024 | 1.65
2025 | 1.56
2026 | 1.47
2027 | 1.38
2028 | 1.29
2029 | 1.2
2030 | 1.11