## generator_info
gen_info_scenario_id | technology_id | technology | min_online_year | fuel | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | distributed | resource_limited | baseload | flexible_baseload | dispatchable | cogen | min_build_capacity | can_build_new | competes_for_space | ccs | storage | storage_efficiency | max_store_rate | max_spinning_reserve_fraction_of_capacity | heat_rate_penalty_spinning_reserve | minimum_loading | deep_cycling_penalty | startup_mmbtu_per_mw | startup_cost_dollars_per_mw | tech_name_again | Notes/DataSource: Black&Veatch 2012 and CEC COG Model Version 2.02-4-5-10 unless otherwise stated
8 | 1 | CCGT | 2010 | Gas | 91289 | 6.705 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3 | CCGT
8 | 103 | CCGT_Cogen | 2010 | Gas | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | CCGT_Cogen | Same as new CCGT, 75% capital cost and fixed cost
8 | 110 | CCGT_Cogen_CCS | 2020 | Gas_CCS | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | CCGT_Cogen_CCS | Same as CCGT_CCS; 75% capital cost and fixed cost
8 | 34 | CCGT_CCS | 2020 | Gas_CCS | 91289 | 10.08 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3 | CCGT_CCS | B&V; the lifetime, construction time, construction cost breakdown, and outage rates are the same as CCGT
8 | 20 | CCGT_EP | 0 | Gas | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3 | CCGT_EP | Same as new CCGT, but with 2008 capital cost
8 | 32 | CCGT_Cogen_EP | 0 | Gas | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | CCGT_Cogen_EP | Same as existing CCGT, 75% capital cost and fixed cost
8 | 2 | Gas_Combustion_Turbine | 2010 | Gas | 91289 | 10.39 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | Gas_Combustion_Turbine
8 | 101 | Gas_Combustion_Turbine_Cogen | 2010 | Gas | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_Cogen | Same as gas combustion turbines, 75% capital cost and fixed cost
8 | 111 | Gas_Combustion_Turbine_Cogen_CCS | 2020 | Gas_CCS | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_Cogen_CCS | Same as gas combustion turbine CCS; 75% capital cost and fixed cost
8 | 35 | Gas_Combustion_Turbine_CCS | 2020 | Gas_CCS | 91289 | 15.6199 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | Gas_Combustion_Turbine_CCS | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for CCGT; we assumed CCS combustion turbine heat rate increases by the same percentage relative to non-CCS combustion turbines as CCS to non-CCS CCGT heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates (varO&M scales with fuel use)
8 | 17 | Gas_Combustion_Turbine_EP | 0 | Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | Gas_Combustion_Turbine_EP | Same as new Combustion Turbine, but with 2008 capital cost
8 | 29 | Gas_Combustion_Turbine_Cogen_EP | 0 | Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Combustion_Turbine_Cogen_EP | Same as existing combustion turbines, 75% capital cost and fixed cost
8 | 104 | Gas_Internal_Combustion_Engine_Cogen | 2010 | Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Internal_Combustion_Engine_Cogen | Same as Gas_Internal_Combustion_Engine_Cogen_EP (which already includes the 75% of capital and fixed costs)
8 | 112 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2020 | Gas_CCS | 91289 |  | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Internal_Combustion_Engine_Cogen_CCS | Same as Gas_Combustion_Turbine_Cogen_CCS
8 | 24 | Gas_Internal_Combustion_Engine_EP | 0 | Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | Gas_Internal_Combustion_Engine_EP | Same as existing gas combustion turbines
8 | 40 | Gas_Internal_Combustion_Engine_Cogen_EP | 0 | Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Internal_Combustion_Engine_Cogen_EP | Same as existing Gas Internal Combustion Engine, 75% capital cost and fixed cost
8 | 102 | Gas_Steam_Turbine_Cogen | 2010 | Gas | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Steam_Turbine_Cogen | Same as existing gas steam turbines, 75% capital cost and fixed cost
8 | 113 | Gas_Steam_Turbine_Cogen_CCS | 2020 | Gas_CCS | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Steam_Turbine_Cogen_CCS | Capital and fixed cost equal to 75% of Gas_Steam_Turbine_EP + difference between CCGT_CCS and CCGT, other flags like Gas_Steam_Turbine_Cogen (except ccs)
8 | 19 | Gas_Steam_Turbine_EP | 0 | Gas | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0.04 | 0.4 | 0.04 | 8.92 | 10.3 | Gas_Steam_Turbine_EP | OGS (Oil Gas Steam) Tidball et al (NREL cost comparison), outage rates from 2006-2010 NERC Generating Availability Report, construction schedule like Coal Steam Turbine
8 | 31 | Gas_Steam_Turbine_Cogen_EP | 0 | Gas | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Gas_Steam_Turbine_Cogen_EP | Same as existing gas steam turbines, 75% capital cost and fixed cost
8 | 60 | DistillateFuelOil_Combustion_Turbine_EP | 0 | DistillateFuelOil | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | DistillateFuelOil_Combustion_Turbine_EP | Same as existing Gas Combustion Turbine
8 | 61 | DistillateFuelOil_Internal_Combustion_Engine_EP | 0 | DistillateFuelOil | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86 | DistillateFuelOil_Internal_Combustion_Engine_EP | Same as existing Gas Combustion Turbine
8 | 12 | Coal_Steam_Turbine | 2010 | Coal | 91289 | 9 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | 0 | 0 | Coal_Steam_Turbine
8 | 39 | Coal_Steam_Turbine_CCS | 2020 | Coal_CCS | 91289 | 12.1 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | 0 | 0 | Coal_Steam_Turbine_CCS
8 | 100 | Coal_Steam_Turbine_Cogen | 2010 | Coal | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_Cogen | Same as new coal steam turbines, 75% capital cost and fixed cost
8 | 117 | Coal_Steam_Turbine_Cogen_CCS | 2020 | Coal_CCS | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_Cogen_CCS | Capital and fixed cost equal to 75% of Coal_Steam_Turbine_CCS
8 | 18 | Coal_Steam_Turbine_EP | 0 | Coal | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.05 | 0 | 0 | Coal_Steam_Turbine_EP | same as coal steam turbine, but using 2008 costs
8 | 30 | Coal_Steam_Turbine_Cogen_EP | 0 | Coal | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Coal_Steam_Turbine_Cogen_EP | Same as existing coal steam turbines, 75% capital cost and fixed cost
8 | 11 | Coal_IGCC | 2010 | Coal | 91289 | 7.95 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | 0 | 0 | Coal_IGCC
8 | 38 | Coal_IGCC_CCS | 2020 | Coal_CCS | 91289 | 10.38 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | 0 | 0 | Coal_IGCC_CCS
8 | 10 | Biomass_IGCC | 2010 | Bio_Solid | 91289 | 12.5 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Biomass_IGCC
8 | 37 | Biomass_IGCC_CCS | 2020 | Bio_Solid_CCS | 91289 | 16.3208 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Biomass_IGCC_CCS | We assumed that the capital cost and fixed cost for adding a CCS system increase by the same amount (per W) as for Coal IGCC; we assumed CCS biomass IGCC heat rate increases by the same percentage relative to non-CCS biomass IGCC as CCS to non-CCS coal IGCC heat rates; we also assume that there's an adder per MWh for variable costs -- we assume that the difference in variable cost scales with the difference in heat rates
8 | 90 | Bio_Solid_Steam_Turbine_EP | 0 | Bio_Solid | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Solid_Steam_Turbine_EP
8 | 91 | Bio_Solid_Steam_Turbine_Cogen_EP | 0 | Bio_Solid | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Solid_Steam_Turbine_Cogen_EP | Same as biomass steam turbine EP, 75% capital cost and fixed cost
8 | 107 | Bio_Solid_Steam_Turbine_Cogen | 2010 | Bio_Solid | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Solid_Steam_Turbine_Cogen | Same as Biomass_IGCC for costs (heat rate derived upstream from here)
8 | 116 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2020 | Bio_Solid_CCS | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Solid_Steam_Turbine_Cogen_CCS | Same as non-ccs version, except for 75% of capex and fixed O&M costs
8 | 8 | Bio_Gas | 2010 | Bio_Gas | 91289 | 13.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Gas | NREL REF/EPRI McGowin 2007
8 | 105 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2010 | Bio_Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Gas_Internal_Combustion_Engine_Cogen | Same as new Biogas, 75% capital cost and fixed cost
8 | 80 | Bio_Gas_Internal_Combustion_Engine_EP | 2010 | Bio_Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Gas_Internal_Combustion_Engine_EP | Same as new Biogas
8 | 81 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 2010 | Bio_Gas | 91289 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | Same as new Biogas, 75% capital cost and fixed cost
8 | 82 | Bio_Gas_Steam_Turbine_EP | 0 | Bio_Gas | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Gas_Steam_Turbine_EP | Everything but costs same as gas steam turbine; captial and fixed costs are assumed to be the gas steam turbine cost plus the difference between biogas and gas combustion turbine, except for VarO&M, which was taken from bio solid steam turbine EP
8 | 85 | Bio_Liquid_Steam_Turbine_Cogen_EP | 0 | Bio_Liquid | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Liquid_Steam_Turbine_Cogen_EP | Same as biomass steam turbine, 75% capital cost and fixed cost
8 | 106 | Bio_Liquid_Steam_Turbine_Cogen | 2010 | Bio_Liquid | 91289 |  | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bio_Liquid_Steam_Turbine_Cogen | Same as biomass steam turbine, 75% capital cost and fixed cost
8 | 22 | Nuclear_EP | 0 | Uranium | 91289 |  | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Nuclear_EP
8 | 13 | Nuclear | 2010 | Uranium | 91289 | 9.72 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Nuclear
8 | 21 | Geothermal_EP | 0 | Geothermal | 91289 |  | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.0075 | 0.0241 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Geothermal_EP
8 | 14 | Geothermal | 2010 | Geothermal | 65639 |  | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.0075 | 0.0241 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Geothermal
8 | 6 | Residential_PV | 2010 | Solar | 0 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Residential_PV
8 | 25 | Commercial_PV | 2010 | Solar | 0 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Commercial_PV
8 | 26 | Central_PV | 2010 | Solar | 65639 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Central_PV
8 | 27 | CSP_Trough_No_Storage | 2010 | Solar | 65639 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CSP_Trough_No_Storage
8 | 7 | CSP_Trough_6h_Storage | 2010 | Solar | 65639 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CSP_Trough_6h_Storage
8 | 23 | Wind_EP | 0 | Wind | 91289 |  | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wind_EP | Same as new wind except for a generic connect cost
8 | 4 | Wind | 2010 | Wind | 65639 |  | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wind
8 | 5 | Offshore_Wind | 2010 | Wind | 65639 |  | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Offshore_Wind | Fixed-Bottom costs used… should split fixed and floating at some point
8 | 15 | Hydro_NonPumped_EP | 0 | Water | 91289 |  | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.05 | 0.019 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hydro_NonPumped_EP
8 | 16 | Hydro_Pumped_EP | 0 | Water | 91289 |  | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.038 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Hydro_Pumped_EP | 0.74 taken as efficiency because it's more representative of existing plants rather than new builds. Also, if you change the efficiency value here, make sure to also change it when calculating hydro monthly flows
8 | 28 | Compressed_Air_Energy_Storage | 2010 | Gas | 91289 | 4.91 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0.817 | 1.2 | 0.5 | 0.1 | 0 | 0 | 0 | 0.86 | Compressed_Air_Energy_Storage | $1,200,000 taken as capital cost in 2010 rather than 2004 based on conversation with Hernandez, also The storage efficiency of the the storage phase of compressed air energy storage from Samir Succar and Robert H. Williams: Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power, p. 39
8 | 33 | Battery_Storage | 2010 | Storage | 91289 |  | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 10 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.75 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Battery_Storage | 10 year lifetime assumed for 100% DoD; see storage_params sheet for sources

## Info CSV for export
gen_info_scenario_id | technology_id | technology | min_online_year | fuel | connect_cost_generic_$2007_per_mw | heat_rate_mbtu_per_mwh | construction_time_years | year_1_cost_fraction | year_2_cost_fraction | year_3_cost_fraction | year_4_cost_fraction | year_5_cost_fraction | year_6_cost_fraction | max_age_years | forced_outage_rate | scheduled_outage_rate | intermittent | distributed | resource_limited | baseload | flexible_baseload | dispatchable | cogen | min_build_capacity | can_build_new | competes_for_space | ccs | storage | storage_efficiency | max_store_rate | max_spinning_reserve_fraction_of_capacity | heat_rate_penalty_spinning_reserve | minimum_loading | deep_cycling_penalty | startup_mmbtu_per_mw | startup_cost_dollars_per_mw
8 | 1 | CCGT | 2010 | Gas | 91289 | 6.705 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3
8 | 2 | Gas_Combustion_Turbine | 2010 | Gas | 91289 | 10.39 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 4 | Wind | 2010 | Wind | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 5 | Offshore_Wind | 2010 | Wind | 65639 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 6 | Residential_PV | 2010 | Solar | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 7 | CSP_Trough_6h_Storage | 2010 | Solar | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 8 | Bio_Gas | 2010 | Bio_Gas | 91289 | 13.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 10 | Biomass_IGCC | 2010 | Bio_Solid | 91289 | 12.5 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 11 | Coal_IGCC | 2010 | Coal | 91289 | 7.95 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | 0 | 0
8 | 12 | Coal_Steam_Turbine | 2010 | Coal | 91289 | 9 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | 0 | 0
8 | 13 | Nuclear | 2010 | Uranium | 91289 | 9.72 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.04 | 0.06 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 14 | Geothermal | 2010 | Geothermal | 65639 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.0075 | 0.0241 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 15 | Hydro_NonPumped_EP | 0 | Water | 91289 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.05 | 0.019 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 16 | Hydro_Pumped_EP | 0 | Water | 91289 | 0 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.038 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.74 | 1 | 0 | 0 | 0 | 0 | 0 | 0
8 | 17 | Gas_Combustion_Turbine_EP | 0 | Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 18 | Coal_Steam_Turbine_EP | 0 | Coal | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.05 | 0 | 0
8 | 19 | Gas_Steam_Turbine_EP | 0 | Gas | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31 | 0.04 | 0.4 | 0.04 | 8.92 | 10.3
8 | 20 | CCGT_EP | 0 | Gas | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3
8 | 21 | Geothermal_EP | 0 | Geothermal | 91289 | 0 | 3 | 0.2 | 0.4 | 0.4 | 0 | 0 | 0 | 30 | 0.0075 | 0.0241 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 22 | Nuclear_EP | 0 | Uranium | 91289 | 0 | 6 | 0.56 | 0.2 | 0.14 | 0.06 | 0.02 | 0.02 | 40 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 23 | Wind_EP | 0 | Wind | 91289 | 0 | 2 | 0.05 | 0.95 | 0 | 0 | 0 | 0 | 30 | 0.05 | 0.006 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 24 | Gas_Internal_Combustion_Engine_EP | 0 | Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 25 | Commercial_PV | 2010 | Solar | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 26 | Central_PV | 2010 | Solar | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.02 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 27 | CSP_Trough_No_Storage | 2010 | Solar | 65639 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.06 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 28 | Compressed_Air_Energy_Storage | 2010 | Gas | 91289 | 4.91 | 6 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 30 | 0.03 | 0.04 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0.817 | 1.2 | 0.5 | 0.1 | 0 | 0 | 0 | 0.86
8 | 29 | Gas_Combustion_Turbine_Cogen_EP | 0 | Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 30 | Coal_Steam_Turbine_Cogen_EP | 0 | Coal | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 31 | Gas_Steam_Turbine_Cogen_EP | 0 | Gas | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 32 | CCGT_Cogen_EP | 0 | Gas | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 33 | Battery_Storage | 2010 | Storage | 91289 | 0 | 3 | 0.8 | 0.1 | 0.1 | 0 | 0 | 0 | 10 | 0.02 | 0.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0.75 | 1 | 0 | 0 | 0 | 0 | 0 | 0
8 | 34 | CCGT_CCS | 2020 | Gas_CCS | 91289 | 10.08 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.38 | 0.33 | 0.4 | 0.33 | 9.16 | 10.3
8 | 35 | Gas_Combustion_Turbine_CCS | 2020 | Gas_CCS | 91289 | 15.6199 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 37 | Biomass_IGCC_CCS | 2020 | Bio_Solid_CCS | 91289 | 16.3208 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 38 | Coal_IGCC_CCS | 2020 | Coal_CCS | 91289 | 10.38 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.08 | 0.12 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.29 | 0 | 0
8 | 39 | Coal_Steam_Turbine_CCS | 2020 | Coal_CCS | 91289 | 12.1 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.05 | 0 | 0
8 | 40 | Gas_Internal_Combustion_Engine_Cogen_EP | 0 | Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 60 | DistillateFuelOil_Combustion_Turbine_EP | 0 | DistillateFuelOil | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 61 | DistillateFuelOil_Internal_Combustion_Engine_EP | 0 | DistillateFuelOil | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 0 | 0 | 0.22 | 0.86
8 | 80 | Bio_Gas_Internal_Combustion_Engine_EP | 2010 | Bio_Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 81 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 2010 | Bio_Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 82 | Bio_Gas_Steam_Turbine_EP | 0 | Bio_Gas | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 85 | Bio_Liquid_Steam_Turbine_Cogen_EP | 0 | Bio_Liquid | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 90 | Bio_Solid_Steam_Turbine_EP | 0 | Bio_Solid | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 91 | Bio_Solid_Steam_Turbine_Cogen_EP | 0 | Bio_Solid | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 100 | Coal_Steam_Turbine_Cogen | 2010 | Coal | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 101 | Gas_Combustion_Turbine_Cogen | 2010 | Gas | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 102 | Gas_Steam_Turbine_Cogen | 2010 | Gas | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 103 | CCGT_Cogen | 2010 | Gas | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 104 | Gas_Internal_Combustion_Engine_Cogen | 2010 | Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 105 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2010 | Bio_Gas | 91289 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0.11 | 0.04 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 106 | Bio_Liquid_Steam_Turbine_Cogen | 2010 | Bio_Liquid | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 107 | Bio_Solid_Steam_Turbine_Cogen | 2010 | Bio_Solid | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 110 | CCGT_Cogen_CCS | 2020 | Gas_CCS | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.04 | 0.06 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 111 | Gas_Combustion_Turbine_Cogen_CCS | 2020 | Gas_CCS | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 112 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2020 | Gas_CCS | 91289 | 0 | 2 | 0.25 | 0.75 | 0 | 0 | 0 | 0 | 20 | 0.03 | 0.05 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 113 | Gas_Steam_Turbine_Cogen_CCS | 2020 | Gas_CCS | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.1288 | 0.0915 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 116 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2020 | Bio_Solid_CCS | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.09 | 0.076 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | 117 | Coal_Steam_Turbine_Cogen_CCS | 2020 | Coal_CCS | 91289 | 0 | 2 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 40 | 0.06 | 0.1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0

## generator_costs
NOTE: existing plants have data from 2008 from the B&V capital cost document… their year is null as these values will represent a range of years of existing plants
note: we assume that cogen plants have 3/4 of the capital cost and fixed cost of a pure-electric plant, (to reflect shared infrastructure for cogen), but the same variable operating costs.
heat rates for cogen are calculated via existing plants so aren't included here
variable o&m for cogen ccs projects are calculated in build wecc cap factors.sql
gen_costs_scenario_id | technology | year | $year_of_costs_data_source | inflation_between_data_source_and_2007 | overnight_cost | fixed_o_m | var_o_m | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | storage_energy_capacity_cost_$2007_per_mwh
10 | CCGT | 2010 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2015 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2020 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2025 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2030 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2035 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2040 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2045 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT | 2050 | 2009 | 0.93 | 1230000 | 6310 | 3.67 | 1143900 | 5868.3 | 3.4131
10 | CCGT_Cogen | 2010 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2015 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2020 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2025 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2030 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2035 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2040 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2045 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_Cogen | 2050 | 2009 | 0.93 | 922500 | 4732.5 | 3.67 | 857925 | 4401.225 | 3.4131
10 | CCGT_EP |  | 2009 | 0.93 | 1250000 | 6310 | 3.67 | 1162500 | 5868.3 | 3.4131
10 | CCGT_Cogen_EP |  | 2009 | 0.93 | 937500 | 4732.5 | 3.67 | 871875 | 4401.225 | 3.4131
10 | CCGT_CCS | 2020 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2025 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2030 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2035 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2040 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2045 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_CCS | 2050 | 2009 | 0.93 | 3750000 | 18400 | 10 | 3487500 | 17112 | 9.3
10 | CCGT_Cogen_CCS | 2020 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2025 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2030 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2035 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2040 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2045 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | CCGT_Cogen_CCS | 2050 | 2009 | 0.93 | 2812500 | 13800 | 10 | 2615625 | 12834 | 9.3
10 | Gas_Combustion_Turbine | 2010 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2015 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2020 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2025 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2030 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2035 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2040 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2045 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine | 2050 | 2009 | 0.93 | 651000 | 5260 | 29.9 | 605430 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2010 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2015 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2020 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2025 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2030 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2035 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2040 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2045 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_Cogen | 2050 | 2009 | 0.93 | 488250 | 3945 | 29.9 | 454072.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_EP |  | 2009 | 0.93 | 671000 | 5260 | 29.9 | 624030 | 4891.8 | 27.807
10 | Gas_Combustion_Turbine_Cogen_EP |  | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Combustion_Turbine_CCS | 2020 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2025 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2030 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2035 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2040 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2045 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_CCS | 2050 | 2009 | 0.93 | 3171000 | 17350 | 49.433 | 2949030 | 16135.5 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2020 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2025 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2030 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2035 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2040 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2045 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Combustion_Turbine_Cogen_CCS | 2050 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_EP |  | 2009 | 0.93 | 671000 | 5260 | 29.9 | 624030 | 4891.8 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen_EP |  | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2010 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2015 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2020 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2025 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2030 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2035 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2040 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2045 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen | 2050 | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2020 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2025 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2030 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2035 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2040 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2045 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2050 | 2009 | 0.93 | 2378250 | 13012.5 | 49.433 | 2211772.5 | 12101.625 | 45.9727
10 | Gas_Steam_Turbine_EP |  | 2004 | 1.1679 | 396000 | 25260 | 3.16 | 462488.4 | 29501.154 | 3.6906
10 | Gas_Steam_Turbine_Cogen_EP |  | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2010 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2015 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2020 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2025 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2030 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2035 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2040 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2045 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen | 2050 | 2004 | 1.1679 | 297000 | 18945 | 3.16 | 346866.3 | 22125.8655 | 3.6906
10 | Gas_Steam_Turbine_Cogen_CCS | 2020 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2025 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2030 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2035 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2040 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2045 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | Gas_Steam_Turbine_Cogen_CCS | 2050 | 2004 | 1.1679 |  |  |  | 2104566.3 | 30558.6405 | 9.5775
10 | DistillateFuelOil_Combustion_Turbine_EP |  | 2009 | 0.93 | 671000 | 5260 | 29.9 | 624030 | 4891.8 | 27.807
10 | DistillateFuelOil_Internal_Combustion_Engine_EP |  | 2009 | 0.93 | 503250 | 3945 | 29.9 | 468022.5 | 3668.85 | 27.807
10 | Coal_Steam_Turbine | 2010 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2015 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2020 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2025 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2030 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2035 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2040 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2045 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine | 2050 | 2009 | 0.93 | 2890000 | 23000 | 3.71 | 2687700 | 21390 | 3.4503
10 | Coal_Steam_Turbine_CCS | 2020 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2025 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2030 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2035 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2040 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2045 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_CCS | 2050 | 2009 | 0.93 | 5640000 | 35200 | 6.02 | 5245200 | 32736 | 5.5986
10 | Coal_Steam_Turbine_Cogen | 2010 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2015 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2020 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2025 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2030 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2035 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2040 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2045 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen | 2050 | 2009 | 0.93 | 2167500 | 17250 | 3.71 | 2015775 | 16042.5 | 3.4503
10 | Coal_Steam_Turbine_Cogen_CCS | 2020 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2025 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2030 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2035 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2040 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2045 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_Cogen_CCS | 2050 | 2009 | 0.93 | 4230000 | 26400 | 6.02 | 3933900 | 24552 | 5.5986
10 | Coal_Steam_Turbine_EP |  | 2009 | 0.93 | 3040000 | 23000 | 3.71 | 2827200 | 21390 | 3.4503
10 | Coal_Steam_Turbine_Cogen_EP |  | 2009 | 0.93 | 2280000 | 17250 | 3.71 | 2120400 | 16042.5 | 3.4503
10 | Coal_IGCC | 2010 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2015 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2020 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2025 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2030 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2035 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2040 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2045 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC | 2050 | 2009 | 0.93 | 4010000 | 31100 | 6.54 | 3729300 | 28923 | 6.0822
10 | Coal_IGCC_CCS | 2020 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2025 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2030 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2035 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2040 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2045 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Coal_IGCC_CCS | 2050 | 2009 | 0.93 | 6600000 | 44400 | 10.6 | 6138000 | 41292 | 9.858
10 | Biomass_IGCC | 2010 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2015 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2020 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2025 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2030 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2035 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2040 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2045 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC | 2050 | 2009 | 0.93 | 3830000 | 95000 | 15 | 3561900 | 88350 | 13.95
10 | Biomass_IGCC_CCS | 2020 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2025 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2030 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2035 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2040 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2045 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Biomass_IGCC_CCS | 2050 | 2009 | 0.93 | 6420000 | 108300 | 21.6459 | 5970600 | 100719 | 20.1307
10 | Bio_Solid_Steam_Turbine_EP |  | 2009 | 0.93 | 4020000 | 95000 | 15 | 3738600 | 88350 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen_EP |  | 2009 | 0.93 | 3015000 | 71250 | 15 | 2803950 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2010 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2015 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2020 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2025 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2030 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2035 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2040 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2045 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen | 2050 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2020 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2025 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2030 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2035 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2040 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2045 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2050 | 2009 | 0.93 | 4815000 | 81225 | 21.6459 | 4477950 | 75539.25 | 20.1307
10 | Bio_Gas | 2010 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2015 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2020 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2025 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2030 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2035 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2040 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2045 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas | 2050 | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2010 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2015 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2020 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2025 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2030 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2035 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2040 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2045 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2050 | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_EP |  | 2010 | 0.9161 | 1915000 | 58200 | 14.5 | 1754331.5 | 53317.02 | 13.2835
10 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP |  | 2010 | 0.9161 | 1436250 | 43650 | 14.5 | 1315748.625 | 39987.765 | 13.2835
10 | Bio_Gas_Steam_Turbine_EP | [6 empty] | 1592789.9 | 77926.374 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen_EP |  | 2009 | 0.93 | 3015000 | 71250 | 15 | 2803950 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2010 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2015 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2020 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2025 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2030 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2035 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2040 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2045 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Bio_Liquid_Steam_Turbine_Cogen | 2050 | 2009 | 0.93 | 2872500 | 71250 | 15 | 2671425 | 66262.5 | 13.95
10 | Nuclear_EP |  | 2009 | 0.93 | 6230000 | 127000 | 0 | 5793900 | 118110 | 0
10 | Nuclear | 2010 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2015 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2020 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2025 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2030 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2035 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2040 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2045 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Nuclear | 2050 | 2009 | 0.93 | 6100000 | 127000 | 0 | 5673000 | 118110 | 0
10 | Geothermal_EP |  | 2009 | 0.93 | 6240000 | 0 | 31 | 5803200 | 0 | 28.83
10 | Geothermal | 2010 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2015 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2020 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2025 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2030 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2035 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2040 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2045 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Geothermal | 2050 | 2009 | 0.93 | 5940000 | 0 | 31 | 5524200 | 0 | 28.83
10 | Residential_PV | 2010 | 2009 | 0.93 | 5950000 | 50000 | 0 | 5533500 | 46500 | 0
10 | Residential_PV | 2015 | 2009 | 0.93 | 4340000 | 48000 | 0 | 4036200 | 44640 | 0
10 | Residential_PV | 2020 | 2009 | 0.93 | 3750000 | 45000 | 0 | 3487500 | 41850 | 0
10 | Residential_PV | 2025 | 2009 | 0.93 | 3460000 | 43000 | 0 | 3217800 | 39990 | 0
10 | Residential_PV | 2030 | 2009 | 0.93 | 3290000 | 41000 | 0 | 3059700 | 38130 | 0
10 | Residential_PV | 2035 | 2009 | 0.93 | 3190000 | 39000 | 0 | 2966700 | 36270 | 0
10 | Residential_PV | 2040 | 2009 | 0.93 | 3090000 | 37000 | 0 | 2873700 | 34410 | 0
10 | Residential_PV | 2045 | 2009 | 0.93 | 3010000 | 35000 | 0 | 2799300 | 32550 | 0
10 | Residential_PV | 2050 | 2009 | 0.93 | 2930000 | 33000 | 0 | 2724900 | 30690 | 0
10 | Commercial_PV | 2010 | 2009 | 0.93 | 4790000 | 50000 | 0 | 4454700 | 46500 | 0
10 | Commercial_PV | 2015 | 2009 | 0.93 | 3840000 | 48000 | 0 | 3571200 | 44640 | 0
10 | Commercial_PV | 2020 | 2009 | 0.93 | 3340000 | 45000 | 0 | 3106200 | 41850 | 0
10 | Commercial_PV | 2025 | 2009 | 0.93 | 3090000 | 43000 | 0 | 2873700 | 39990 | 0
10 | Commercial_PV | 2030 | 2009 | 0.93 | 2960000 | 41000 | 0 | 2752800 | 38130 | 0
10 | Commercial_PV | 2035 | 2009 | 0.93 | 2860000 | 39000 | 0 | 2659800 | 36270 | 0
10 | Commercial_PV | 2040 | 2009 | 0.93 | 2770000 | 37000 | 0 | 2576100 | 34410 | 0
10 | Commercial_PV | 2045 | 2009 | 0.93 | 2690000 | 35000 | 0 | 2501700 | 32550 | 0
10 | Commercial_PV | 2050 | 2009 | 0.93 | 2620000 | 33000 | 0 | 2436600 | 30690 | 0
10 | Central_PV | 2010 | 2009 | 0.93 | 3000000 | 50000 | 0 | 2790000 | 46500 | 0
10 | Central_PV | 2015 | 2009 | 0.93 | 2620000 | 48000 | 0 | 2436600 | 44640 | 0
10 | Central_PV | 2020 | 2009 | 0.93 | 2510000 | 45000 | 0 | 2334300 | 41850 | 0
10 | Central_PV | 2025 | 2009 | 0.93 | 2410000 | 43000 | 0 | 2241300 | 39990 | 0
10 | Central_PV | 2030 | 2009 | 0.93 | 2310000 | 41000 | 0 | 2148300 | 38130 | 0
10 | Central_PV | 2035 | 2009 | 0.93 | 2230000 | 39000 | 0 | 2073900 | 36270 | 0
10 | Central_PV | 2040 | 2009 | 0.93 | 2160000 | 37000 | 0 | 2008800 | 34410 | 0
10 | Central_PV | 2045 | 2009 | 0.93 | 2090000 | 35000 | 0 | 1943700 | 32550 | 0
10 | Central_PV | 2050 | 2009 | 0.93 | 2030000 | 33000 | 0 | 1887900 | 30690 | 0
10 | CSP_Trough_No_Storage | 2010 | 2009 | 0.93 | 4910000 | 50000 | 0 | 4566300 | 46500 | 0
10 | CSP_Trough_No_Storage | 2015 | 2009 | 0.93 | 4720000 | 50000 | 0 | 4389600 | 46500 | 0
10 | CSP_Trough_No_Storage | 2020 | 2009 | 0.93 | 4540000 | 50000 | 0 | 4222200 | 46500 | 0
10 | CSP_Trough_No_Storage | 2025 | 2009 | 0.93 | 4350000 | 50000 | 0 | 4045500 | 46500 | 0
10 | CSP_Trough_No_Storage | 2030 | 2009 | 0.93 | 4170000 | 50000 | 0 | 3878100 | 46500 | 0
10 | CSP_Trough_No_Storage | 2035 | 2009 | 0.93 | 3987000 | 50000 | 0 | 3707910 | 46500 | 0
10 | CSP_Trough_No_Storage | 2040 | 2009 | 0.93 | 3800000 | 50000 | 0 | 3534000 | 46500 | 0
10 | CSP_Trough_No_Storage | 2045 | 2009 | 0.93 | 3620000 | 50000 | 0 | 3366600 | 46500 | 0
10 | CSP_Trough_No_Storage | 2050 | 2009 | 0.93 | 3430000 | 50000 | 0 | 3189900 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2010 | 2009 | 0.93 | 7060000 | 50000 | 0 | 6565800 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2015 | 2009 | 0.93 | 6800000 | 50000 | 0 | 6324000 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2020 | 2009 | 0.93 | 6530000 | 50000 | 0 | 6072900 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2025 | 2009 | 0.93 | 5920000 | 50000 | 0 | 5505600 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2030 | 2009 | 0.93 | 5310000 | 50000 | 0 | 4938300 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2035 | 2009 | 0.93 | 4700000 | 50000 | 0 | 4371000 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2040 | 2009 | 0.93 | 4700000 | 50000 | 0 | 4371000 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2045 | 2009 | 0.93 | 4700000 | 50000 | 0 | 4371000 | 46500 | 0
10 | CSP_Trough_6h_Storage | 2050 | 2009 | 0.93 | 4700000 | 50000 | 0 | 4371000 | 46500 | 0
10 | Wind_EP |  | 2009 | 0.93 | 2060000 | 60000 | 0 | 1915800 | 55800 | 0
10 | Wind | 2010 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2015 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2020 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2025 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2030 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2035 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2040 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2045 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Wind | 2050 | 2009 | 0.93 | 1980000 | 60000 | 0 | 1841400 | 55800 | 0
10 | Offshore_Wind | 2010 | 2009 | 0.93 | 3310000 | 100000 | 0 | 3078300 | 93000 | 0
10 | Offshore_Wind | 2015 | 2009 | 0.93 | 3230000 | 100000 | 0 | 3003900 | 93000 | 0
10 | Offshore_Wind | 2020 | 2009 | 0.93 | 3150000 | 100000 | 0 | 2929500 | 93000 | 0
10 | Offshore_Wind | 2025 | 2009 | 0.93 | 3070000 | 100000 | 0 | 2855100 | 93000 | 0
10 | Offshore_Wind | 2030 | 2009 | 0.93 | 2990000 | 100000 | 0 | 2780700 | 93000 | 0
10 | Offshore_Wind | 2035 | 2009 | 0.93 | 2990000 | 100000 | 0 | 2780700 | 93000 | 0
10 | Offshore_Wind | 2040 | 2009 | 0.93 | 2990000 | 100000 | 0 | 2780700 | 93000 | 0
10 | Offshore_Wind | 2045 | 2009 | 0.93 | 2990000 | 100000 | 0 | 2780700 | 93000 | 0
10 | Offshore_Wind | 2050 | 2009 | 0.93 | 2990000 | 100000 | 0 | 2780700 | 93000 | 0
10 | Hydro_NonPumped_EP |  | 2009 | 0.93 | 3600000 | 15000 | 6 | 3348000 | 13950 | 5.58
10 | Hydro_Pumped_EP |  | 2009 | 0.93 | 2230000 | 30800 | 0 | 2073900 | 28644 | 0
10 | Compressed_Air_Energy_Storage | 2010 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2015 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2020 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2025 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2030 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2035 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2040 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2045 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2050 | 2009 | 0.93 |  | 11600 | 1.55 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Battery_Storage | 2010 | 2009 | 0.93 |  | 25200 |  | 967588.0052 | 23436 | 0 | 338655.8018
10 | Battery_Storage | 2015 | 2009 | 0.93 |  | 25200 |  | 943337.6793 | 23436 | 0 | 330168.1877
10 | Battery_Storage | 2020 | 2009 | 0.93 |  | 25200 |  | 919087.3533 | 23436 | 0 | 321680.5737
10 | Battery_Storage | 2025 | 2009 | 0.93 |  | 25200 |  | 894837.0274 | 23436 | 0 | 313192.9596
10 | Battery_Storage | 2030 | 2009 | 0.93 |  | 25200 |  | 870586.7014 | 23436 | 0 | 304705.3455
10 | Battery_Storage | 2035 | 2009 | 0.93 |  | 25200 |  | 846336.3755 | 23436 | 0 | 296217.7314
10 | Battery_Storage | 2040 | 2009 | 0.93 |  | 25200 |  | 822086.0495 | 23436 | 0 | 287730.1173
10 | Battery_Storage | 2045 | 2009 | 0.93 |  | 25200 |  | 797835.7236 | 23436 | 0 | 279242.5033
10 | Battery_Storage | 2050 | 2009 | 0.93 |  | 25200 |  | 773585.3977 | 23436 | 0 | 270754.8892

## Costs CSV for export
gen_costs_scenario_id | technology | year | overnight_cost_$2007 | fixed_o_m_$2007 | var_o_m_$2007 | storage_energy_capacity_cost_$2007_per_mwh
10 | CCGT | 2010 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2015 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2020 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2025 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2030 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2035 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2040 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2045 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT | 2050 | 1143900 | 5868.3 | 3.4131 | 0
10 | CCGT_Cogen | 2010 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2015 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2020 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2025 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2030 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2035 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2040 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2045 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_Cogen | 2050 | 857925 | 4401.225 | 3.4131 | 0
10 | CCGT_EP | 0 | 1162500 | 5868.3 | 3.4131 | 0
10 | CCGT_Cogen_EP | 0 | 871875 | 4401.225 | 3.4131 | 0
10 | CCGT_CCS | 2020 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2025 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2030 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2035 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2040 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2045 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_CCS | 2050 | 3487500 | 17112 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2020 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2025 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2030 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2035 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2040 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2045 | 2615625 | 12834 | 9.3 | 0
10 | CCGT_Cogen_CCS | 2050 | 2615625 | 12834 | 9.3 | 0
10 | Gas_Combustion_Turbine | 2010 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2015 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2020 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2025 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2030 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2035 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2040 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2045 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine | 2050 | 605430 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2010 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2015 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2020 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2025 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2030 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2035 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2040 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2045 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen | 2050 | 454072.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_EP | 0 | 624030 | 4891.8 | 27.807 | 0
10 | Gas_Combustion_Turbine_Cogen_EP | 0 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Combustion_Turbine_CCS | 2020 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2025 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2030 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2035 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2040 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2045 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_CCS | 2050 | 2949030 | 16135.5 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2020 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2025 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2030 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2035 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2040 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2045 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Combustion_Turbine_Cogen_CCS | 2050 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_EP | 0 | 624030 | 4891.8 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_EP | 0 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2010 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2015 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2020 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2025 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2030 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2035 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2040 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2045 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen | 2050 | 468022.5 | 3668.85 | 27.807 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2020 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2025 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2030 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2035 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2040 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2045 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Internal_Combustion_Engine_Cogen_CCS | 2050 | 2211772.5 | 12101.625 | 45.9727 | 0
10 | Gas_Steam_Turbine_EP | 0 | 462488.4 | 29501.154 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen_EP | 0 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2010 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2015 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2020 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2025 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2030 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2035 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2040 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2045 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen | 2050 | 346866.3 | 22125.8655 | 3.6906 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2020 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2025 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2030 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2035 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2040 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2045 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | Gas_Steam_Turbine_Cogen_CCS | 2050 | 2104566.3 | 30558.6405 | 9.5775 | 0
10 | DistillateFuelOil_Combustion_Turbine_EP | 0 | 624030 | 4891.8 | 27.807 | 0
10 | DistillateFuelOil_Internal_Combustion_Engine_EP | 0 | 468022.5 | 3668.85 | 27.807 | 0
10 | Coal_Steam_Turbine | 2010 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2015 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2020 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2025 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2030 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2035 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2040 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2045 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine | 2050 | 2687700 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine_CCS | 2020 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2025 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2030 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2035 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2040 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2045 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_CCS | 2050 | 5245200 | 32736 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen | 2010 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2015 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2020 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2025 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2030 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2035 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2040 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2045 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen | 2050 | 2015775 | 16042.5 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2020 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2025 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2030 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2035 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2040 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2045 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_Cogen_CCS | 2050 | 3933900 | 24552 | 5.5986 | 0
10 | Coal_Steam_Turbine_EP | 0 | 2827200 | 21390 | 3.4503 | 0
10 | Coal_Steam_Turbine_Cogen_EP | 0 | 2120400 | 16042.5 | 3.4503 | 0
10 | Coal_IGCC | 2010 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2015 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2020 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2025 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2030 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2035 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2040 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2045 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC | 2050 | 3729300 | 28923 | 6.0822 | 0
10 | Coal_IGCC_CCS | 2020 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2025 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2030 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2035 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2040 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2045 | 6138000 | 41292 | 9.858 | 0
10 | Coal_IGCC_CCS | 2050 | 6138000 | 41292 | 9.858 | 0
10 | Biomass_IGCC | 2010 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2015 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2020 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2025 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2030 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2035 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2040 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2045 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC | 2050 | 3561900 | 88350 | 13.95 | 0
10 | Biomass_IGCC_CCS | 2020 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2025 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2030 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2035 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2040 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2045 | 5970600 | 100719 | 20.1307 | 0
10 | Biomass_IGCC_CCS | 2050 | 5970600 | 100719 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_EP | 0 | 3738600 | 88350 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_EP | 0 | 2803950 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2010 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2015 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2020 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2025 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2030 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2035 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2040 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2045 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen | 2050 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2020 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2025 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2030 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2035 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2040 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2045 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Solid_Steam_Turbine_Cogen_CCS | 2050 | 4477950 | 75539.25 | 20.1307 | 0
10 | Bio_Gas | 2010 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2015 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2020 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2025 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2030 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2035 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2040 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2045 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas | 2050 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2010 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2015 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2020 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2025 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2030 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2035 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2040 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2045 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen | 2050 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_EP | 0 | 1754331.5 | 53317.02 | 13.2835 | 0
10 | Bio_Gas_Internal_Combustion_Engine_Cogen_EP | 0 | 1315748.625 | 39987.765 | 13.2835 | 0
10 | Bio_Gas_Steam_Turbine_EP | 0 | 1592789.9 | 77926.374 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen_EP | 0 | 2803950 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2010 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2015 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2020 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2025 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2030 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2035 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2040 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2045 | 2671425 | 66262.5 | 13.95 | 0
10 | Bio_Liquid_Steam_Turbine_Cogen | 2050 | 2671425 | 66262.5 | 13.95 | 0
10 | Nuclear_EP | 0 | 5793900 | 118110 | 0 | 0
10 | Nuclear | 2010 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2015 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2020 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2025 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2030 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2035 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2040 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2045 | 5673000 | 118110 | 0 | 0
10 | Nuclear | 2050 | 5673000 | 118110 | 0 | 0
10 | Geothermal_EP | 0 | 5803200 | 0 | 28.83 | 0
10 | Geothermal | 2010 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2015 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2020 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2025 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2030 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2035 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2040 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2045 | 5524200 | 0 | 28.83 | 0
10 | Geothermal | 2050 | 5524200 | 0 | 28.83 | 0
10 | Residential_PV | 2010 | 5533500 | 46500 | 0 | 0
10 | Residential_PV | 2015 | 4036200 | 44640 | 0 | 0
10 | Residential_PV | 2020 | 3487500 | 41850 | 0 | 0
10 | Residential_PV | 2025 | 3217800 | 39990 | 0 | 0
10 | Residential_PV | 2030 | 3059700 | 38130 | 0 | 0
10 | Residential_PV | 2035 | 2966700 | 36270 | 0 | 0
10 | Residential_PV | 2040 | 2873700 | 34410 | 0 | 0
10 | Residential_PV | 2045 | 2799300 | 32550 | 0 | 0
10 | Residential_PV | 2050 | 2724900 | 30690 | 0 | 0
10 | Commercial_PV | 2010 | 4454700 | 46500 | 0 | 0
10 | Commercial_PV | 2015 | 3571200 | 44640 | 0 | 0
10 | Commercial_PV | 2020 | 3106200 | 41850 | 0 | 0
10 | Commercial_PV | 2025 | 2873700 | 39990 | 0 | 0
10 | Commercial_PV | 2030 | 2752800 | 38130 | 0 | 0
10 | Commercial_PV | 2035 | 2659800 | 36270 | 0 | 0
10 | Commercial_PV | 2040 | 2576100 | 34410 | 0 | 0
10 | Commercial_PV | 2045 | 2501700 | 32550 | 0 | 0
10 | Commercial_PV | 2050 | 2436600 | 30690 | 0 | 0
10 | Central_PV | 2010 | 2790000 | 46500 | 0 | 0
10 | Central_PV | 2015 | 2436600 | 44640 | 0 | 0
10 | Central_PV | 2020 | 2334300 | 41850 | 0 | 0
10 | Central_PV | 2025 | 2241300 | 39990 | 0 | 0
10 | Central_PV | 2030 | 2148300 | 38130 | 0 | 0
10 | Central_PV | 2035 | 2073900 | 36270 | 0 | 0
10 | Central_PV | 2040 | 2008800 | 34410 | 0 | 0
10 | Central_PV | 2045 | 1943700 | 32550 | 0 | 0
10 | Central_PV | 2050 | 1887900 | 30690 | 0 | 0
10 | CSP_Trough_No_Storage | 2010 | 4566300 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2015 | 4389600 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2020 | 4222200 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2025 | 4045500 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2030 | 3878100 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2035 | 3707910 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2040 | 3534000 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2045 | 3366600 | 46500 | 0 | 0
10 | CSP_Trough_No_Storage | 2050 | 3189900 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2010 | 6565800 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2015 | 6324000 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2020 | 6072900 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2025 | 5505600 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2030 | 4938300 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2035 | 4371000 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2040 | 4371000 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2045 | 4371000 | 46500 | 0 | 0
10 | CSP_Trough_6h_Storage | 2050 | 4371000 | 46500 | 0 | 0
10 | Wind_EP | 0 | 1915800 | 55800 | 0 | 0
10 | Wind | 2010 | 1841400 | 55800 | 0 | 0
10 | Wind | 2015 | 1841400 | 55800 | 0 | 0
10 | Wind | 2020 | 1841400 | 55800 | 0 | 0
10 | Wind | 2025 | 1841400 | 55800 | 0 | 0
10 | Wind | 2030 | 1841400 | 55800 | 0 | 0
10 | Wind | 2035 | 1841400 | 55800 | 0 | 0
10 | Wind | 2040 | 1841400 | 55800 | 0 | 0
10 | Wind | 2045 | 1841400 | 55800 | 0 | 0
10 | Wind | 2050 | 1841400 | 55800 | 0 | 0
10 | Offshore_Wind | 2010 | 3078300 | 93000 | 0 | 0
10 | Offshore_Wind | 2015 | 3003900 | 93000 | 0 | 0
10 | Offshore_Wind | 2020 | 2929500 | 93000 | 0 | 0
10 | Offshore_Wind | 2025 | 2855100 | 93000 | 0 | 0
10 | Offshore_Wind | 2030 | 2780700 | 93000 | 0 | 0
10 | Offshore_Wind | 2035 | 2780700 | 93000 | 0 | 0
10 | Offshore_Wind | 2040 | 2780700 | 93000 | 0 | 0
10 | Offshore_Wind | 2045 | 2780700 | 93000 | 0 | 0
10 | Offshore_Wind | 2050 | 2780700 | 93000 | 0 | 0
10 | Hydro_NonPumped_EP | 0 | 3348000 | 13950 | 5.58 | 0
10 | Hydro_Pumped_EP | 0 | 2073900 | 28644 | 0 | 0
10 | Compressed_Air_Energy_Storage | 2010 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2015 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2020 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2025 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2030 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2035 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2040 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2045 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Compressed_Air_Energy_Storage | 2050 | 763416.6667 | 10788 | 1.4415 | 19085.4167
10 | Battery_Storage | 2010 | 967588.0052 | 23436 | 0 | 338655.8018
10 | Battery_Storage | 2015 | 943337.6793 | 23436 | 0 | 330168.1877
10 | Battery_Storage | 2020 | 919087.3533 | 23436 | 0 | 321680.5737
10 | Battery_Storage | 2025 | 894837.0274 | 23436 | 0 | 313192.9596
10 | Battery_Storage | 2030 | 870586.7014 | 23436 | 0 | 304705.3455
10 | Battery_Storage | 2035 | 846336.3755 | 23436 | 0 | 296217.7314
10 | Battery_Storage | 2040 | 822086.0495 | 23436 | 0 | 287730.1173
10 | Battery_Storage | 2045 | 797835.7236 | 23436 | 0 | 279242.5033
10 | Battery_Storage | 2050 | 773585.3977 | 23436 | 0 | 270754.8892

## spinning_reserves_penalty
Switch equivalent | Heat rate at percent of full load |  |  |  | 1-min ramp rate | 10-min ramp rate | heat_rate_penalty_spinning_reserve | Note
| 25% | 50% | 75% | 100%
CCGT | 1.788 | 1.195 | 1.102 | 1 | 0.038 | 0.38 | 0.32674
Gas_Steam_Turbine | 1.276 | 1.061 | 1.01 | 1 | 0.031 | 0.31 | 0.036287
Gas_Combustion_Turbine | 1.504 | 1.095 | 1.029 | 1 | 0.135 | 1 | 0.10024 | We assume that a combustion turbine will never run at part load lower than 50 percent, so the 10-min ramp rate used to calculate the heat rate penalty is 0.5 rather than 1.
Sources
Heat rate curve | Structure and Performance of Six European Wholesale Electricity Markets in 2003, 2004, and 2005. Appendix I. DG Comp. Presented to DG Comp 26th February 2007
Ramp rates | WWSIS, p. 174
|  | Part load relative heat rate |  |  | Heat rate penalty |  |  |  | Extra Fuel D | Extra Fuel (Sp)
Percent of full load | Spinning reserve provided | CCGT | Steam | Combustion | CCGT | Steam | Combustion |  | CCGT | CCGT
100% | 0% | 1 | 1 | 1 | #DIV/0! | #DIV/0! | #DIV/0! |  | 0 | #DIV/0!
99% | 1% | 1.0041 | 1.0004 | 1.0012 | 0.40392 | 0.0396 | 0.11484 |  | 0.028274 | 0.028274
98% | 2% | 1.0082 | 1.0008 | 1.0023 | 0.39984 | 0.0392 | 0.11368 |  | 0.055978 | 0.055978
97% | 3% | 1.0122 | 1.0012 | 1.0035 | 0.39576 | 0.0388 | 0.11252 |  | 0.08311 | 0.08311
96% | 4% | 1.0163 | 1.0016 | 1.0046 | 0.39168 | 0.0384 | 0.11136 |  | 0.10967 | 0.10967
95% | 5% | 1.0204 | 1.002 | 1.0058 | 0.3876 | 0.038 | 0.1102 |  | 0.13566 | 0.13566
94% | 6% | 1.0245 | 1.0024 | 1.007 | 0.38352 | 0.0376 | 0.10904 |  | 0.16108 | 0.16108
93% | 7% | 1.0286 | 1.0028 | 1.0081 | 0.37944 | 0.0372 | 0.10788 |  | 0.18593 | 0.18593
92% | 8% | 1.0326 | 1.0032 | 1.0093 | 0.37536 | 0.0368 | 0.10672 |  | 0.2102 | 0.2102
91% | 9% | 1.0367 | 1.0036 | 1.0104 | 0.37128 | 0.0364 | 0.10556 |  | 0.23391 | 0.23391
90% | 10% | 1.0408 | 1.004 | 1.0116 | 0.3672 | 0.036 | 0.1044 |  | 0.25704 | 0.25704
89% | 11% | 1.0449 | 1.0044 | 1.0128 | 0.36312 | 0.0356 | 0.10324 |  | 0.2796 | 0.2796
88% | 12% | 1.049 | 1.0048 | 1.0139 | 0.35904 | 0.0352 | 0.10208 |  | 0.30159 | 0.30159
87% | 13% | 1.053 | 1.0052 | 1.0151 | 0.35496 | 0.0348 | 0.10092 |  | 0.32301 | 0.32301
86% | 14% | 1.0571 | 1.0056 | 1.0162 | 0.35088 | 0.0344 | 0.09976 |  | 0.34386 | 0.34386
85% | 15% | 1.0612 | 1.006 | 1.0174 | 0.3468 | 0.034 | 0.0986 |  | 0.36414 | 0.36414
84% | 16% | 1.0653 | 1.0064 | 1.0186 | 0.34272 | 0.0336 | 0.09744 |  | 0.38385 | 0.38385
83% | 17% | 1.0694 | 1.0068 | 1.0197 | 0.33864 | 0.0332 | 0.09628 |  | 0.40298 | 0.40298
82% | 18% | 1.0734 | 1.0072 | 1.0209 | 0.33456 | 0.0328 | 0.09512 |  | 0.42155 | 0.42155
81% | 19% | 1.0775 | 1.0076 | 1.022 | 0.33048 | 0.0324 | 0.09396 |  | 0.43954 | 0.43954
80% | 20% | 1.0816 | 1.008 | 1.0232 | 0.3264 | 0.032 | 0.0928 |  | 0.45696 | 0.45696
79% | 21% | 1.0857 | 1.0084 | 1.0244 | 0.32232 | 0.0316 | 0.09164 |  | 0.47381 | 0.47381
78% | 22% | 1.0898 | 1.0088 | 1.0255 | 0.31824 | 0.0312 | 0.09048 |  | 0.49009 | 0.49009
77% | 23% | 1.0938 | 1.0092 | 1.0267 | 0.31416 | 0.0308 | 0.08932 |  | 0.5058 | 0.5058
76% | 24% | 1.0979 | 1.0096 | 1.0278 | 0.31008 | 0.0304 | 0.08816 |  | 0.52093 | 0.52093
75% | 25% | 1.102 | 1.01 | 1.029 | 0.306 | 0.03 | 0.087 |  | 0.5355 | 0.5355
74% | 26% | 1.1057 | 1.012 | 1.0316 | 0.3009 | 0.034268 | 0.090052 |  | 0.54763 | 0.54763
73% | 27% | 1.1094 | 1.0141 | 1.0343 | 0.29589 | 0.038068 | 0.092683 |  | 0.55924 | 0.55924
72% | 28% | 1.1132 | 1.0161 | 1.0369 | 0.29098 | 0.041451 | 0.094937 |  | 0.57033 | 0.57033
71% | 29% | 1.1169 | 1.0182 | 1.0396 | 0.28615 | 0.044461 | 0.096854 |  | 0.58089 | 0.58089
70% | 30% | 1.1206 | 1.0202 | 1.0422 | 0.2814 | 0.047133 | 0.098467 |  | 0.59094 | 0.59094
69% | 31% | 1.1243 | 1.0222 | 1.0448 | 0.27671 | 0.049502 | 0.099805 |  | 0.60047 | 0.60047
68% | 32% | 1.128 | 1.0243 | 1.0475 | 0.27209 | 0.051595 | 0.10089 |  | 0.60947 | 0.60947
67% | 33% | 1.1318 | 1.0263 | 1.0501 | 0.26751 | 0.053438 | 0.10176 |  | 0.61795 | 0.61795
66% | 34% | 1.1355 | 1.0284 | 1.0528 | 0.26299 | 0.055052 | 0.10242 |  | 0.62592 | 0.62592
65% | 35% | 1.1392 | 1.0304 | 1.0554 | 0.25851 | 0.056457 | 0.10289 |  | 0.63336 | 0.63336
64% | 36% | 1.1429 | 1.0324 | 1.058 | 0.25408 | 0.057671 | 0.10318 |  | 0.64028 | 0.64028
63% | 37% | 1.1466 | 1.0345 | 1.0607 | 0.24968 | 0.058709 | 0.10332 |  | 0.64668 | 0.64668
62% | 38% | 1.1504 | 1.0365 | 1.0633 | 0.24532 | 0.059585 | 0.10331 |  | 0.65256 | 0.65256
61% | 39% | 1.1541 | 1.0386 | 1.066 | 0.241 | 0.060312 | 0.10317 |  | 0.65792 | 0.65792
60% | 40% | 1.1578 | 1.0406 | 1.0686 | 0.2367 | 0.0609 | 0.1029 |  | 0.66276 | 0.66276
59% | 41% | 1.1615 | 1.0426 | 1.0712 | 0.23243 | 0.06136 | 0.10252 |  | 0.66708 | 0.66708
58% | 42% | 1.1652 | 1.0447 | 1.0739 | 0.22819 | 0.061701 | 0.10202 |  | 0.67087 | 0.67087
57% | 43% | 1.169 | 1.0467 | 1.0765 | 0.22397 | 0.061931 | 0.10143 |  | 0.67415 | 0.67415
56% | 44% | 1.1727 | 1.0488 | 1.0792 | 0.21977 | 0.062058 | 0.10075 |  | 0.67691 | 0.67691
55% | 45% | 1.1764 | 1.0508 | 1.0818 | 0.2156 | 0.062089 | 0.099978 |  | 0.67914 | 0.67914
54% | 46% | 1.1801 | 1.0528 | 1.0844 | 0.21145 | 0.06203 | 0.099125 |  | 0.68085 | 0.68085
53% | 47% | 1.1838 | 1.0549 | 1.0871 | 0.20731 | 0.061886 | 0.098197 |  | 0.68205 | 0.68205
52% | 48% | 1.1876 | 1.0569 | 1.0897 | 0.20319 | 0.061663 | 0.097197 |  | 0.68272 | 0.68272
51% | 49% | 1.1913 | 1.059 | 1.0924 | 0.19909 | 0.061367 | 0.09613 |  | 0.68287 | 0.68287
50% | 50% | 1.195 | 1.061 | 1.095 | 0.195 | 0.061 | 0.095 |  | 0.6825 | 0.6825
49% | 51% | 1.2187 | 1.0696 | 1.1114 | 0.21014 | 0.066871 | 0.10699
48% | 52% | 1.2424 | 1.0782 | 1.1277 | 0.22379 | 0.072185 | 0.1179
47% | 53% | 1.2662 | 1.0868 | 1.1441 | 0.23603 | 0.076974 | 0.12777
46% | 54% | 1.2899 | 1.0954 | 1.1604 | 0.24693 | 0.081267 | 0.13667
45% | 55% | 1.3136 | 1.104 | 1.1768 | 0.25658 | 0.085091 | 0.14465 |  |  |  | The penalty factor applied is calculated as follows:
44% | 56% | 1.3373 | 1.1126 | 1.1932 | 0.26504 | 0.088471 | 0.15177
43% | 57% | 1.361 | 1.1212 | 1.2095 | 0.27236 | 0.091432 | 0.15806 |  |  |  | Fuel use as represented by SWITCH = Actual fuel use
42% | 58% | 1.3848 | 1.1298 | 1.2259 | 0.27862 | 0.093993 | 0.16357 |  |  |  | DispatchGen x heat_rate + ProvideSpinningReserve x penalty x heat_rate = DispatchGen x degraded_heat_rate
41% | 59% | 1.4085 | 1.1384 | 1.2422 | 0.28386 | 0.096176 | 0.16834
40% | 60% | 1.4322 | 1.147 | 1.2586 | 0.28813 | 0.098 | 0.1724 |  |  |  | Assuming DispatchGen + ProvideSpinningReserve = Installed_Capacity and normalizing for installed capacity, this gives us:
39% | 61% | 1.4559 | 1.1556 | 1.275 | 0.29149 | 0.099482 | 0.17579
38% | 62% | 1.4796 | 1.1642 | 1.2913 | 0.29397 | 0.10064 | 0.17855 |  |  |  | ( DispatchGen x heat_rate + (Installed_Capacity – DispatchGen) x penalty x heat_rate) / Installed_Capacity = DispatchGen x degraded_heat_rate / Installed_Capacity
37% | 63% | 1.5034 | 1.1728 | 1.3077 | 0.29562 | 0.10149 | 0.1807
36% | 64% | 1.5271 | 1.1814 | 1.324 | 0.29648 | 0.10204 | 0.18227 |  |  |  | fraction_dispatched x heat_rate + (1 – fraction_dispatched) x penalty x heat_rate = fraction_dispatched x degraded_heat_rate
35% | 65% | 1.5508 | 1.19 | 1.3404 | 0.29658 | 0.10231 | 0.18329
34% | 66% | 1.5745 | 1.1986 | 1.3568 | 0.29596 | 0.10231 | 0.18379 |  |  |  | penalty = ( fraction_dispatched x (degraded_heat_rate – heat_rate ) ) / ( (1 – fraction_dispatched ) x heat_rate )
33% | 67% | 1.5982 | 1.2072 | 1.3731 | 0.29466 | 0.10205 | 0.18378
32% | 68% | 1.622 | 1.2158 | 1.3895 | 0.29269 | 0.10155 | 0.18328
31% | 69% | 1.6457 | 1.2244 | 1.4058 | 0.29009 | 0.10082 | 0.18233
30% | 70% | 1.6694 | 1.233 | 1.4222 | 0.28689 | 0.099857 | 0.18094
29% | 71% | 1.6931 | 1.2416 | 1.4386 | 0.28311 | 0.098682 | 0.17913
28% | 72% | 1.7168 | 1.2502 | 1.4549 | 0.27877 | 0.0973 | 0.17691
27% | 73% | 1.7406 | 1.2588 | 1.4713 | 0.27391 | 0.095721 | 0.17431
26% | 74% | 1.7643 | 1.2674 | 1.4876 | 0.26853 | 0.093951 | 0.17133
25% | 75% | 1.788 | 1.276 | 1.504 | 0.26267 | 0.092 | 0.168

## deep_cycling_penalty
Switch equivalent | Heat rate at percent of full load |  |  |  | 1-min ramp rate | 10-min ramp rate | Note
| 25% | 50% | 75% | 100%
CCGT | 1.788 | 1.195 | 1.102 | 1 | 0.038 | 0.38
Gas_Steam_Turbine | 1.276 | 1.061 | 1.01 | 1 | 0.031 | 0.31
Gas_Combustion_Turbine | 1.504 | 1.095 | 1.029 | 1 | 0.135 | 1 | We assume that a combustion turbine will never run at part load lower than 50 percent, so the 10-min ramp rate used to calculate the heat rate penalty is 0.5 rather than 1.
Sources
Heat rate curve | Structure and Performance of Six European Wholesale Electricity Markets in 2003, 2004, and 2005. Appendix I. DG Comp. Presented to DG Comp 26th February 2007
Ramp rates | WWSIS, p. 174
| Part load relative heat rate |  |  | Partial loading penalty |  |  | Average penalty up to 40 percent loading
Percent of full load | CCGT | Steam | Combustion | CCGT | Steam | Combustion | CCGT | Steam | Combustion
100% | 1 | 1 | 1 | #DIV/0! | #DIV/0! | #DIV/0! | 0.29291 | 0.051769 | 0.10767
99% | 1.0041 | 1.0004 | 1.0012 | 0.40392 | 0.0396 | 0.11484
98% | 1.0082 | 1.0008 | 1.0023 | 0.39984 | 0.0392 | 0.11368
97% | 1.0122 | 1.0012 | 1.0035 | 0.39576 | 0.0388 | 0.11252
96% | 1.0163 | 1.0016 | 1.0046 | 0.39168 | 0.0384 | 0.11136
95% | 1.0204 | 1.002 | 1.0058 | 0.3876 | 0.038 | 0.1102
94% | 1.0245 | 1.0024 | 1.007 | 0.38352 | 0.0376 | 0.10904
93% | 1.0286 | 1.0028 | 1.0081 | 0.37944 | 0.0372 | 0.10788
92% | 1.0326 | 1.0032 | 1.0093 | 0.37536 | 0.0368 | 0.10672
91% | 1.0367 | 1.0036 | 1.0104 | 0.37128 | 0.0364 | 0.10556
90% | 1.0408 | 1.004 | 1.0116 | 0.3672 | 0.036 | 0.1044
89% | 1.0449 | 1.0044 | 1.0128 | 0.36312 | 0.0356 | 0.10324
88% | 1.049 | 1.0048 | 1.0139 | 0.35904 | 0.0352 | 0.10208
87% | 1.053 | 1.0052 | 1.0151 | 0.35496 | 0.0348 | 0.10092
86% | 1.0571 | 1.0056 | 1.0162 | 0.35088 | 0.0344 | 0.09976
85% | 1.0612 | 1.006 | 1.0174 | 0.3468 | 0.034 | 0.0986
84% | 1.0653 | 1.0064 | 1.0186 | 0.34272 | 0.0336 | 0.09744
83% | 1.0694 | 1.0068 | 1.0197 | 0.33864 | 0.0332 | 0.09628
82% | 1.0734 | 1.0072 | 1.0209 | 0.33456 | 0.0328 | 0.09512
81% | 1.0775 | 1.0076 | 1.022 | 0.33048 | 0.0324 | 0.09396
80% | 1.0816 | 1.008 | 1.0232 | 0.3264 | 0.032 | 0.0928
79% | 1.0857 | 1.0084 | 1.0244 | 0.32232 | 0.0316 | 0.09164
78% | 1.0898 | 1.0088 | 1.0255 | 0.31824 | 0.0312 | 0.09048
77% | 1.0938 | 1.0092 | 1.0267 | 0.31416 | 0.0308 | 0.08932
76% | 1.0979 | 1.0096 | 1.0278 | 0.31008 | 0.0304 | 0.08816
75% | 1.102 | 1.01 | 1.029 | 0.306 | 0.03 | 0.087
74% | 1.1057 | 1.012 | 1.0316 | 0.3009 | 0.034268 | 0.090052
73% | 1.1094 | 1.0141 | 1.0343 | 0.29589 | 0.038068 | 0.092683
72% | 1.1132 | 1.0161 | 1.0369 | 0.29098 | 0.041451 | 0.094937
71% | 1.1169 | 1.0182 | 1.0396 | 0.28615 | 0.044461 | 0.096854
70% | 1.1206 | 1.0202 | 1.0422 | 0.2814 | 0.047133 | 0.098467
69% | 1.1243 | 1.0222 | 1.0448 | 0.27671 | 0.049502 | 0.099805
68% | 1.128 | 1.0243 | 1.0475 | 0.27209 | 0.051595 | 0.10089
67% | 1.1318 | 1.0263 | 1.0501 | 0.26751 | 0.053438 | 0.10176
66% | 1.1355 | 1.0284 | 1.0528 | 0.26299 | 0.055052 | 0.10242
65% | 1.1392 | 1.0304 | 1.0554 | 0.25851 | 0.056457 | 0.10289
64% | 1.1429 | 1.0324 | 1.058 | 0.25408 | 0.057671 | 0.10318
63% | 1.1466 | 1.0345 | 1.0607 | 0.24968 | 0.058709 | 0.10332
62% | 1.1504 | 1.0365 | 1.0633 | 0.24532 | 0.059585 | 0.10331
61% | 1.1541 | 1.0386 | 1.066 | 0.241 | 0.060312 | 0.10317
60% | 1.1578 | 1.0406 | 1.0686 | 0.2367 | 0.0609 | 0.1029
59% | 1.1615 | 1.0426 | 1.0712 | 0.23243 | 0.06136 | 0.10252
58% | 1.1652 | 1.0447 | 1.0739 | 0.22819 | 0.061701 | 0.10202
57% | 1.169 | 1.0467 | 1.0765 | 0.22397 | 0.061931 | 0.10143
56% | 1.1727 | 1.0488 | 1.0792 | 0.21977 | 0.062058 | 0.10075 |  |  | The penalty factor applied is calculated as follows:
55% | 1.1764 | 1.0508 | 1.0818 | 0.2156 | 0.062089 | 0.099978
54% | 1.1801 | 1.0528 | 1.0844 | 0.21145 | 0.06203 | 0.099125 |  |  | Fuel use as represented by SWITCH = Actual fuel use
53% | 1.1838 | 1.0549 | 1.0871 | 0.20731 | 0.061886 | 0.098197 |  |  | DispatchGen x heat_rate + (Installed_Capacity – DispatchGen) x penalty x heat_rate = DispatchGen x degraded_heat_rate
52% | 1.1876 | 1.0569 | 1.0897 | 0.20319 | 0.061663 | 0.097197
51% | 1.1913 | 1.059 | 1.0924 | 0.19909 | 0.061367 | 0.09613 |  |  | Normalizing for installed capacity, this gives us:
50% | 1.195 | 1.061 | 1.095 | 0.195 | 0.061 | 0.095
49% | 1.2183 | 1.0696 | 1.1114 | 0.20976 | 0.066871 | 0.10699 |  |  | ( DispatchGen x heat_rate + (Installed_Capacity – DispatchGen) x penalty x heat_rate) / Installed_Capacity = DispatchGen x degraded_heat_rate / Installed_Capacity
48% | 1.2416 | 1.0782 | 1.1277 | 0.22305 | 0.072185 | 0.1179
47% | 1.265 | 1.0868 | 1.1441 | 0.23496 | 0.076974 | 0.12777 |  |  | fraction_dispatched x heat_rate + (1 – fraction_dispatched) x penalty x heat_rate = fraction_dispatched x degraded_heat_rate
46% | 1.2883 | 1.0954 | 1.1604 | 0.24557 | 0.081267 | 0.13667
45% | 1.3116 | 1.104 | 1.1768 | 0.25495 | 0.085091 | 0.14465 |  |  | penalty = ( fraction_dispatched x (degraded_heat_rate – heat_rate ) ) / ( (1 – fraction_dispatched ) x heat_rate )
44% | 1.3349 | 1.1126 | 1.1932 | 0.26315 | 0.088471 | 0.15177
43% | 1.3582 | 1.1212 | 1.2095 | 0.27025 | 0.091432 | 0.15806
42% | 1.3816 | 1.1298 | 1.2259 | 0.2763 | 0.093993 | 0.16357
41% | 1.4049 | 1.1384 | 1.2422 | 0.28136 | 0.096176 | 0.16834
40% | 1.4282 | 1.147 | 1.2586 | 0.28547 | 0.098 | 0.1724
39% | 1.4515 | 1.1556 | 1.275 | 0.28868 | 0.099482 | 0.17579
38% | 1.4748 | 1.1642 | 1.2913 | 0.29103 | 0.10064 | 0.17855
37% | 1.4982 | 1.1728 | 1.3077 | 0.29257 | 0.10149 | 0.1807
36% | 1.5215 | 1.1814 | 1.324 | 0.29333 | 0.10204 | 0.18227
35% | 1.5448 | 1.19 | 1.3404 | 0.29335 | 0.10231 | 0.18329
34% | 1.5681 | 1.1986 | 1.3568 | 0.29267 | 0.10231 | 0.18379
33% | 1.5914 | 1.2072 | 1.3731 | 0.29131 | 0.10205 | 0.18378
32% | 1.6148 | 1.2158 | 1.3895 | 0.2893 | 0.10155 | 0.18328
31% | 1.6381 | 1.2244 | 1.4058 | 0.28667 | 0.10082 | 0.18233
30% | 1.6614 | 1.233 | 1.4222 | 0.28346 | 0.099857 | 0.18094
29% | 1.6847 | 1.2416 | 1.4386 | 0.27967 | 0.098682 | 0.17913
28% | 1.708 | 1.2502 | 1.4549 | 0.27535 | 0.0973 | 0.17691
27% | 1.7314 | 1.2588 | 1.4713 | 0.2705 | 0.095721 | 0.17431
26% | 1.7547 | 1.2674 | 1.4876 | 0.26516 | 0.093951 | 0.17133
25% | 1.778 | 1.276 | 1.504 | 0.25933 | 0.092 | 0.168

## storage_params
Battery lifetime and variable costs
Sources: | Rahul Walawalker phd thesis: NaS cycle life is 5000 to 20000, service life is 12-20 yrs (p. 21)
EPRI 2010 storage technology options paper: "The estimated life of a sodium-sulfur battery is approximately 15 years after 4500 cycles at 90% depth of discharge."
PNNL; Lu, N., et al., “The Wide-Area Energy Storage and Management System – Battery Storage Evaluation”
Method: | Assume no battery replacement in variable costs
Assume battery lifetime of 10 years at the 100% depth of discharge currently allowed by SWITCH
Assume frequent utilization: an average of just under one cycle per day (3142/(10*365) for the 100% DoD case), so might be a good idea to check number of cycles after the optimization
Battery capital costs
Let x be the per MW cost. Then:
Source: | B&V | [8 empty] | 7.2*x+58.32*0.35x = total cost
Method: | Take total plant cost from B&V and assume per unit power to per unit energy cost ratio of $1000/kW and $350/kWh stays constant over time | [8 empty] | x = total cost/27.612
Year | Power Capacity | Duration | Energy Capacity | Total cost per MW (for 7.2MW, 8.1h system) | Total plant cost (for 7.2MW, 8.1h system) | Power cost | Energy cost | Check | Per unit power to | Power cost | Energy cost
Unit | MW | h | MWh | $/MW-capacity | $ | 2009$/MW power capacity | 2009$/MWh energy capacity |  | per unit capacity ratio | 2007$/MW power capacity | 2007$/MWh energy capacity
2010 | 7.2 | 8.1 | 58.32 | 3990000 | 28728000 | 1040417.2099 | 364146.0235 | ok | 2.8571 | 967588.0052 | 338655.8018
2015 | 7.2 | 8.1 | 58.32 | 3890000 | 28008000 | 1014341.5906 | 355019.5567 | ok | 2.8571 | 943337.6793 | 330168.1877
2020 | 7.2 | 8.1 | 58.32 | 3790000 | 27288000 | 988265.9713 | 345893.09 | ok | 2.8571 | 919087.3533 | 321680.5737
2025 | 7.2 | 8.1 | 58.32 | 3690000 | 26568000 | 962190.352 | 336766.6232 | ok | 2.8571 | 894837.0274 | 313192.9596
2030 | 7.2 | 8.1 | 58.32 | 3590000 | 25848000 | 936114.7327 | 327640.1565 | ok | 2.8571 | 870586.7014 | 304705.3455
2035 | 7.2 | 8.1 | 58.32 | 3490000 | 25128000 | 910039.1134 | 318513.6897 | ok | 2.8571 | 846336.3755 | 296217.7314
2040 | 7.2 | 8.1 | 58.32 | 3390000 | 24408000 | 883963.4941 | 309387.2229 | ok | 2.8571 | 822086.0495 | 287730.1173
2045 | 7.2 | 8.1 | 58.32 | 3290000 | 23688000 | 857887.8748 | 300260.7562 | ok | 2.8571 | 797835.7236 | 279242.5033
2050 | 7.2 | 8.1 | 58.32 | 3190000 | 22968000 | 831812.2555 | 291134.2894 | ok | 2.8571 | 773585.3977 | 270754.8892
CAES capital costs
Source: | EPRI 2010 storage technology options paper: "The estimated life of a sodium-sulfur battery is approximately 15 years after 4500 cycles at 90% depth of discharge."
Method: | Take the difference in cost between a 135MW plant with 20h and 8h of storage; calculate the per MWh-energy-capacity cost; subtract storage energy cost from total cost, divide by power capacity to get the per MW power capacity cost
Year | Power Capacity | Duration | Energy Capacity | Total cost per MW (for 135MW, 8 or 20h system)) | Total cost per MWh (for 135MW, 8 or 20h system)) | Total plant cost
| MW | h | MWh | 2010$/MW-capacity | 2010$/MWh-energy | 2010$ (calculated from capacity) | 2010$ (calculated from energy)
2010 | 135 | 8 | 1080 | 1000000 | 125000 | 135000000 | 135000000
2010 | 135 | 20 | 2700 | 1250000 | 62500 | 168750000 | 168750000
Energy capacity difference between 20h and 8h plant [MWh]
1620
Additional cost for 20h plant [$2010]
33750000
Energy cost [$2010/MWh energy capacity]
20833.3333
| Total energy capacity cost [$2010] | Total power capacity cost
8h | 22500000 | 112500000
20h | 56250000 | 112500000
Power cost [$2010/MW power capacity]
8h | 833333.3333
20h | 833333.3333
Final
Power cost | Energy cost
2007$/MW power capacity | 2007$/MWh energy capacity
763416.6667 | 19085.4167
Note on F50: Ana Mileva: This was actually 60000 in the original data, but I changed it to 62500 to ensure that the total cost calculation matches between capacity and energy (60000*2700<>135*125000)